## BUILDING
PUMP HEAD CALCULATION SHEET
Prject name: | [8 empty] | Pages |  | of
DATE
Project No. |  |  |  |  | REVISION |  |  |  | ENGINEER
Consultant: | [9 empty] | PIPE CONSTRUCTION
Supplier: | [9 empty] | Medium Steel Pipe
Designation
Location: | [14 empty] | Building flow | 275 | worst case
|  | l/s |  | KPa |  |  |  | l/s |  |  | KPa
Spec duty |  | 20 |  |  |  | Actual |  |  |  |  | 170 |  |  |  | 56.874 | ft
|  |  | PIPE |  |  | LENGTH. OR | PRESS | No. | TOTAL | PROGRESSIVE
DESCRIPTION |  | SECT | SIZE | FLOW | VEL | EQUIVELENT | DROP | OFF | P.D | PRESS. DROP | REMARKS | DIA | AREA | Flow
/ ITEM |  | -ION | mm | l/s | m/s | m | kPa/m |  | kPa | kPa |  | m | m | GPM
Inside Mech. Room | SUPPLY
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 1.2 | 0.1294 | 1 | 0.15529 |  | F Hoirzontal pipe |  |  | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1459 | 2.06 | 0.1294 | 1 | 0.26657 |  | F - Bend to pipe header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 0.5 | 0.1294 | 1 | 0.064702 |  | F - Horizontal Pipe |  |  | 137
Tee - Line |  | A | 100 | 8.6433 | 1.1459 | 2.44 | 0.1294 | 1 | 0.31575 |  | F - Bend to pipe header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 2 | 0.1294 | 1 | 0.25881 |  | F - To pump suction |  |  | 137
Isolation Valve | PUMP | A | 100 | 8.6433 | 1.1459 | 1.37 | 0.1294 | 1 | 0.17728 |  | F - Isolation Valve |  |  | 137
Strainer |  | A | 100 | 8.6433 | 1.1459 |  | 0.1294 | 1 | 15 |  | F - Strainer |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 5 | 0.1294 | 1 | 0.64702 |  | F - From pump discharge to Header |  |  | 137
Non Return Valve |  | A | 100 | 8.6433 | 1.1459 | 12.1 | 0.1294 | 1 | 1.5658 |  | F - From pump discharge | 0.0036545 | 1.0489e-05 | 137
Isolation Valve |  | A | 100 | 8.6433 | 1.1459 | 1.37 | 0.1294 | 1 | 0.17728 |  | F - From pump discharge | 0.0013787 | 1.4929e-06 | 137
Straight pipe | SUPPLY | A | 100 | 8.6433 | 1.1459 | 0.5 | 0.1294 | 1 | 0.064702 |  | F - to discharge header |  |  | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1459 | 2.06 | 0.1294 | 1 | 0.26657 |  | F - Bend to pipe header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 1 | 0.1294 | 1 | 0.1294 |  | F - Vertical pipe exiting ground |  |  | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1459 | 2.06 | 0.1294 | 1 | 0.26657 |  | F - Bend to pipe header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 0.5 | 0.1294 | 1 | 0.064702 |  | F - horizontal pipe exiting ground |  |  | 137
Tee - Branch |  | A | 100 | 8.6433 | 1.1459 | 6.4 | 0.1294 | 1 | 0.82819 |  | F - Tee to main header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 0.5 | 0.1294 | 1 | 0.064702 |  | F - Horizontal pipe |  |  | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1459 | 2.06 | 0.1294 | 1 | 0.26657 |  | F - Bend to pipe header |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 0.5 | 0.1294 | 1 | 0.064702 |  | F - Horizontal Pipe |  |  | 137
Air Dirt Separator |  | A | 100 | 8.6433 | 1.1459 |  | 0.1294 | 1 | 5 |  | F - Air dirt separator |  |  | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1459 | 3.3 | 0.1294 | 1 | 0.42704 |  | F & R - Vertical pipe exiting ground |  |  | 137
Tee - Branch |  | A | 100 | 8.6433 | 1.1459 | 6.4 | 0.1294 | 1 | 0.82819 |  | F - Tee to main header |  |  | 137
Straight pipe | RETURN | A | 100 | 14.8892 | 1.9739 | 3.4 | 0.3543 | 1 | 1.2046 |  | R - Horizontal Pipe to HEX header |  |  | 236
90 R Bend |  | A | 100 | 14.8892 | 1.9739 | 2.06 | 0.3543 | 1 | 0.72987 |  | R - Bend to pipe header |  |  | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9739 | 3.4 | 0.3543 | 1 | 1.2046 |  | R - Horizontal Pipe to header |  |  | 236
90 R Bend |  | A | 100 | 14.8892 | 1.9739 | 2.06 | 0.3543 | 1 | 0.72987 |  | R- Bend to pipe header |  |  | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9739 | 7 | 0.3543 | 1 | 2.4801 |  | R - Horizontal Pipe to HEX header |  |  | 236
Tee - Branch |  | A | 100 | 14.8892 | 1.9739 | 6.4 | 0.3543 | 1 | 2.2676 |  | F & R - header take off |  |  | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9739 | 5 | 0.3543 | 1 | 1.7715 |  | F - To pump suction |  |  | 236
Tee - Branch |  | A | 100 | 5.6781 | 0.75277 | 6.4 | 0.059429 | 1 | 0.38035 |  | F - to discharge header | 0.0021923 | 3.7748e-06 | 90
Straight pipe | F & R | A | 80 | 5.6781 | 1.3566 | 3 | 0.25265 | 2 | 1.5159 |  | F & R - straight pipe inside plantroom | 0.0021878 | 3.7594e-06 | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3566 | 1.52 | 0.25265 | 2 | 0.76805 |  | F &R - Bends inside Mech room | 0.0015809 | 1.9629e-06 | 90
Straight pipe |  | A | 80 | 5.6781 | 1.3566 | 7 | 0.25265 | 2 | 3.5371 |  | F & R - Return inside Mech room | 0.0031932 | 8.0082e-06 | 90
Isolation Valve |  | A | 80 | 5.6781 | 1.3566 | 0.97 | 0.25265 | 2 | 0.49014 |  | F & R- Isolation Valve | 0.0012598 | 1.2464e-06 | 90
Straight pipe |  | A | 80 | 5.6781 | 1.3566 | 1 | 0.25265 | 2 | 0.5053 |  | F & R - Return inside Mech room | 0.0012797 | 1.2862e-06 | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3566 | 1.52 | 0.25265 | 2 | 0.76805 | 45.2529 | F & R - Bends inside Mech room to upper | 0.0015809 | 1.9629e-06 | 90 | 15.1395 | ft
[10 empty] | 45.2529 |  | #VALUE! | #VALUE!
Inside building | [11 empty] | #VALUE! | #VALUE!
Straight pipe |  | A | 80 | 5.6781 | 1.3566 | 40 | 0.25265 | 2 | 20.2118 |  | F & R - length of 5" pipework | 0.0065993 | 3.4205e-05 | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3566 | 1.52 | 0.25265 | 7 | 2.6882 |  | F & R - bends of 5" pipework | 0.0015809 | 1.9629e-06 | 90
Isolation Valve |  | A | 80 | 5.6781 | 1.3566 | 0.97 | 0.25265 | 2 | 0.49014 |  | F - isolation into apartment |  |  | 90
Tee - Branch |  | A | 80 | 3.8819 | 0.9275 | 4.57 | 0.12492 | 2 | 1.1418 |  | F & R - T lines of 5" pipework |  |  | 61.53
Tee - Line |  | A | 80 | 0.25236 | 0.060295 | 1.54 | 0.00079118 | 3 | 0.0036552 |  | F & R - T lines of 5" pipework |  |  | 4
Tee - Line |  | A | 80 | 0.13943 | 0.033313 | 1.54 | 0.00026368 | 2 | 0.00081213 |  | F & R - T lines of 5" pipework |  |  | 2.21
Straight pipe |  | A | 80 | 3.8819 | 0.9275 | 3.5 | 0.12492 | 2 | 0.87447 |  | F & R - length of 5" pipework | 0.0019041 | 2.8475e-06 | 61.53
Straight pipe |  | A | 80 | 3.6296 | 0.8672 | 2 | 0.1103 | 2 | 0.44121 |  | F & R - length of 5" pipework | 0.0014259 | 1.5969e-06 | 57.53
Straight pipe |  | A | 80 | 3.4901 | 0.83389 | 3 | 0.10258 | 2 | 0.6155 |  | F & R - length of 5" pipework | 0.0016761 | 2.2064e-06 | 55.32
Straight pipe |  | A | 80 | 3.0983 | 0.74028 | 4 | 0.082282 | 2 | 0.65826 |  | F & R - length of 5" pipework | 0.0017775 | 2.4814e-06 | 49.11
Reducer |  | A | 65 | 2.846 | 0.97383 | 0.85 | 0.17077 | 2 | 0.29032 |  | F & R - Reducer 5" to 4" |  |  | 45.11
Straight pipe |  | A | 80 | 2.846 | 0.67998 | 1 | 0.070303 | 2 | 0.14061 |  | F & R - length of 5" pipework | 0.00090475 | 6.429e-07 | 45.11
Straight pipe |  | A | 80 | 2.7066 | 0.64667 | 1 | 0.064057 | 2 | 0.12811 |  | F & R - length of 5" pipework | 0.00088141 | 6.1016e-07 | 42.9
Balance valve |  | A | 65 | 2.7066 | 0.92612 |  | 0.1556 | 2 | 3 |  | R - balance into apartment |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 1 | 0.1556 | 2 | 0.31121 |  | F & R - length of 4" pipework |  |  | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92612 | 1.35 | 0.1556 | 2 | 0.42013 |  | F & R - bends of 4" pipework |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 1.5 | 0.1556 | 2 | 0.46681 |  | F & R - length of 4" pipework |  |  | 42.9
Tee - Branch |  | A | 65 | 2.3495 | 0.80393 | 3.65 | 0.11973 | 2 | 0.87406 |  | F & R - Horizontal |  |  | 37.24
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 1 | 0.1556 | 2 | 0.31121 |  | F & R - length of 4" pipework |  |  | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92612 | 1.35 | 0.1556 | 2 | 0.42013 |  | F & R - bends of 4" pipework |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 1 | 0.1556 | 2 | 0.31121 |  | F & R - length of 4" pipework |  |  | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92612 | 1.35 | 0.1556 | 2 | 0.42013 |  | F & R - bends of 4" pipework |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 3.5 | 0.1556 | 2 | 1.0892 |  | F & R - Vertical pipework to retail |  |  | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92612 | 1.35 | 0.1556 | 2 | 0.42013 |  | F & R Vertical elbow at level 0 |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 0.5 | 0.1556 | 2 | 0.1556 |  | F & R - Vertical pipework to retail |  |  | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92612 | 1.35 | 0.1556 | 2 | 0.42013 |  | F & R horizontal elbow at level 0 |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 0.5 | 0.1556 | 2 | 0.1556 |  | F & R - Vertical pipework at retail |  |  | 42.9
Tee - Branch |  | A | 65 | 2.7066 | 0.92612 | 3.65 | 0.1556 | 2 | 1.1359 |  | F & R - Horizontal pipework to retail |  |  | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92612 | 0.5 | 0.1556 | 2 | 0.1556 |  | F & R - Horizontal pipework to retail |  |  | 42.9
Tee - Branch |  | A | 50 | 1.8649 | 1.0306 | 3.04 | 0.25087 | 2 | 1.5253 |  | F & R - Horizontal pipework to retail |  |  | 29.56
Straight pipe |  | A | 65 | 1.8649 | 0.63814 | 4.3 | 0.078065 | 2 | 0.67136 |  | F & R - Horizontal pipework to retail |  |  | 29.56
Tee - Line |  | A | 40 | 0.40378 | 0.39668 | 0.79 | 0.060659 | 2 | 0.095842 |  | F & R - Horizontal pipework to retail |  |  | 6.4
Straight pipe |  | A | 65 | 1.4612 | 0.49998 | 8.5 | 0.049683 | 2 | 0.84461 |  | F & R - Horizontal pipework to retail |  |  | 23.16
Tee - Line |  | A | 40 | 0.40378 | 0.39668 | 0.79 | 0.060659 | 2 | 0.095842 |  | F & R - Horizontal pipework to retail |  |  | 6.4
Straight pipe |  | A | 65 | 0.80755 | 0.27633 | 9.5 | 0.016568 | 2 | 0.31479 |  | F & R - Horizontal pipework to retail |  |  | 12.8
Tee - Line |  | A | 40 | 0.40378 | 0.39668 | 0.79 | 0.060659 | 2 | 0.095842 |  | F & R - Horizontal pipework to retail |  |  | 6.4
Reducer |  | A | 40 | 0.40378 | 0.39668 | 0.53 | 0.060659 | 2 | 0.064299 |  | F & R - Horizontal pipework to retail |  |  | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.39668 | 9 | 0.060659 | 2 | 1.0919 |  | F & R - Horizontal pipework to retail |  |  | 6.4
90 R Bend |  | A | 65 | 0.40378 | 0.13816 | 1.35 | 0.0045894 | 2 | 0.012391 |  | F & R - Horizontal bends to retail |  |  | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.39668 | 9 | 0.060659 | 2 | 1.0919 |  | F & R - Horizontal pipework to retail |  |  | 6.4
90 R Bend |  | A | 65 | 0.40378 | 0.13816 | 1.35 | 0.0045894 | 2 | 0.012391 |  | F & R - Horizontal bends to retail |  |  | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.39668 | 9 | 0.060659 | 2 | 1.0919 |  | F & R - Horizontal pipework to retail |  |  | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.39668 | 9 | 0.060659 | 2 | 1.0919 | 45.852 |  |  |  | 6.4 | 15.3399 | ft
91.1049
Index AHU
Strainer |  | A | 40 | 0.40378 | 0.39668 |  | 0.060659 | 1 | 15 |  | F - Coil Strainer |  |  | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.39668 | 0.53 | 0.060659 | 1 | 0.032149 |  | F - Isolation valve |  |  | 6.4
Cooling coil |  | A | 40 | 0.40378 | 0.39668 |  | 0.060659 | 1 | 20 |  | COOLING COIL |  |  | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.39668 | 0.53 | 0.060659 | 1 | 0.032149 |  | R - Isolation valve 1 |  |  | 6.4
Tee - Line |  | A | 40 | 0.40378 | 0.39668 | 0.79 | 0.060659 | 1 | 0.047921 |  | R - Bypass takeoff |  |  | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.39668 | 0.53 | 0.060659 | 1 | 0.032149 |  | R - Isolation valve 2 | 0.00050389 | 1.9942e-07 | 6.4
Control Valve |  | A | 40 | 0.40378 | 0.39668 |  | 0.060659 | 1 | 20 |  | COIL CONTROL VALVE |  |  | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.39668 | 0.53 | 0.060659 | 1 | 0.032149 |  | R - Isolation valve 2 |  |  | 6.4
Tee - Line |  | A | 40 | 0.40378 | 0.39668 | 0.79 | 0.060659 | 1 | 0.047921 |  | R - Bypass takeoff |  |  | 6.4
Balance valve |  | A | 40 | 0.40378 | 0.39668 |  | 0.060659 | 1 | 5 | 60.2244 | R - line balance valve | #VALUE! | #VALUE! | 6.4 | 20.1483 | ft
[10 empty] | 151.3294 |  | #VALUE! | #VALUE! |  | 50.6277 | ft
[12 empty] | #VALUE! | #VALUE!
[5 empty] | SUB-TOTAL |  |  |  | 151.3294
NOTES: |  |  |  |  | SAFETY |  | 10% |  | 15.1329
[5 empty] | TOTAL P.D |  | kPa |  | 166.4623
[8 empty] | SUPPLIER |  |  | MODEL No.
MODEL SPECIFIED
MODEL SELECTED
Note on A12: ONLY ONE FITTING OR STRAIGHT LENGTH PER LINE. NOT BOTH !!

## Data
size | B90 | IV | TeeLine | TeeBend | Reducer | Non Ret. | Reducer 1/2 | Check Vlv | Strainer |  | KV | Valve Size
15 | 0.3 | 0.21 | 0.3 | 0.92 | 0.21 | 1.9 | 0.25 | 0.9 | 15 | 61.188 | 0.16 | 15
20 | 0.42 | 0.27 | 0.42 | 1.26 | 0.27 | 2.15 | 0.4 | 1.6 | 20 | 19.638 | 0.25 | 15
25 | 0.54 | 0.3 | 0.51 | 1.52 | 0.3 | 3 | 0.46 | 1.8 | 25 | 7.875 | 0.4 | 15
32 | 0.71 | 0.46 | 0.7 | 2.1 | 0.46 | 4.26 | 0.66 | 2.07 | 32 | 2.85 | 0.63 | 15
40 | 0.79 | 0.53 | 0.79 | 2.44 | 0.53 | 4.9 | 0.8 | 3.05 | 40 | 1.45 | 1 | 15
50 | 1 | 0.7 | 1 | 3.04 | 0.7 | 6 | 0.98 | 4.2 | 50 | 0.5365 | 1.6 | 15
65 | 1.35 | 0.85 | 1.29 | 3.65 | 0.85 | 7.6 | 1.3 | 5.2 | 65 | 0.25 | 2.5 | 15
80 | 1.52 | 0.97 | 1.54 | 4.57 | 0.97 | 9.2 | 1.5 | 6.2 | 80 | 0.1118 | 4 | 15
100 | 2.06 | 1.37 | 2.44 | 6.4 | 1.37 | 12.1 | 2 | 8.2 | 100 | 0.034 | 6.3 | 20
125 | 2.32 | 1.84 | 2.58 | 7.62 | 1.84 | 15.2 | 2.5 | 10.2 | 125 | 0.015 | 10 | 25
150 | 3 | 2.13 | 3.1 | 9.2 | 2.13 | 18.2 | 3 | 12.8 | 150 | 0.0045 | 16 | 32
200 | 3.9 | 2.74 | 4 | 12.2 | 2.74 | 24.4 | 4 | 17 | 200 | 0.00145 | 25 | 40
250 | 4.9 | 3.68 | 4.9 | 15.4 | 3.68 | 30.7 | 5 | 21 |  |  | 40 | 50
300 | 5.8 | 3.98 | 5.8 | 18.5 | 3.98 | 36.9 | 5.8 | 24.5 |  |  | 63 | 65
350 | 7 | 4.8 | 7 | 20.7 | 5.4 | 41.5 | 7 | 29 |  |  | 100 | 80
400 | 7.9 | 5.4 | 7.9 | 23.3 | 6 | 46.15 | 7.6 | 33 |  |  | 160 | 100
450 | 8.84 | 6 | 8.8 | 26 | 7 | 50.76 | 8.8 | 37 |  |  | 250 | 125
500 | 10.1 | 6.5 | 10.1 | 30.4 | 7.5 | 61.53 | 9.5 | 41 |  |  | 400 | 150
550 | 11.1 | 7.4 | 11.1 | 32.5 | 8.4 | 68 | 11 | 45
600 | 12.2 | 8 | 12.2 | 35.1 | 9 | 73.84 | 12 | 48
|  | 3 | 4 | 5 | 6 | 7 | 6
[5 empty] | ecc |  | conc

## Vel Head loss
| L/S | 20.24
| Suction | 80 | mm |  | VH loss | 1.0709 | meters
| Discharge | 65 | mm |  | VH loss | 10.7093 | Kpa
|  | Q | N | H
|  | Flow | Speed | Head
|  | l/s | RPM | M
|  | 80 | 1440 | 30
Change in speed |  | 69 | 1242 | 22.3172

## data base (hidden)
description / item | consultant's | engineer's | pipe medium's | Pipe data
90 R Bend | Bassett's | C.Dearling | A.B.S (Thermoplastic - Class 4.5) |  | A.B.S (Thermoplastic - Class 4.5) |  |  |  | A.B.S (Thermoplastic - Class 6) |  |  |  | A.B.S (Thermoplastic - Class 9) |  |  |  | A.B.S (Thermoplastic - Class 10) |  |  |  | A.B.S (Thermoplastic - Class 12) |  |  |  | A.B.S (Thermoplastic - Class 15) |  |  |  | Coes-therm |  |  |  | Copper tube (Type A) |  |  |  | Copper tube (Type B)
Isolation Valve | Civil & Civic | C.Pinder | A.B.S (Thermoplastic - Class 6) | nominal | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass
Tee - Line | EMF Griffith's | L.Ramah | A.B.S (Thermoplastic - Class 9) | dia | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m
Tee - Branch | Lincolne Scott | M.Loveday | A.B.S (Thermoplastic - Class 10) | 15 | [20 empty] | 17.1 | 2.1 | 1500 | 0.14 |  |  |  |  | 12.7 | 1.02 | 6380 |  | 10.84
Reducer | Mienhardt | J.Smith | A.B.S (Thermoplastic - Class 12) | 20 | [20 empty] | 21.4 | 2.7 | 1500 | 0.22 |  |  |  |  | 19.05 | 1.42 | 5900
Non Return Valve | Q Build |  | A.B.S (Thermoplastic - Class 15) | 25 | [8 empty] | 29.4 | 2.1 | 900 | 0.23 | [8 empty] | 26.9 | 3.3 | 1500 | 0.35 |  |  |  |  | 25.4 | 1.63 | 5070
Chiller | WBM |  | Coes-therm | 32 | [8 empty] | 37 | 2.6 | 900 | 0.35 | [8 empty] | 34 | 4.1 | 1500 | 0.55 |  |  |  |  | 31.75 | 1.63 | 4010
Control Valve | N D Y |  | Copper tube (Type A) | 40 | [8 empty] | 42.3 | 3 | 900 | 0.45 | [8 empty] | 38.8 | 4.7 | 1500 | 0.7 |  |  |  |  | 38.1 | 1.63 | 3310
Cooling coil |  |  | Copper tube (Type B) | 50 | [8 empty] | 53 | 3.7 | 900 | 0.7 |  |  |  |  | 50.8 | 4.8 | 1200 | 0.9 | [8 empty] | 50.8 | 1.63 | 2460
Annubar |  |  | Galv Steel Pipe (Medium) | 65 | [20 empty] | 48.6 | 5.9 | 1500 | 1.1 |  |  |  |  | 63.5 | 1.63 | 1960
Griswald Valve |  |  | Heavy Steel Pipe | 80 |  |  |  |  | 81.5 | 3.7 | 600 | 1.1 | 78.1 | 5.4 | 900 | 1.6 |  |  |  |  | 74.9 | 7 | 1200 | 2 | 71.7 | 8.6 | 1500 | 2.4 |  |  |  |  | 76.2 | 2.03 | 2030
Straight pipe |  |  | Light Steel Pipe | 100 |  |  |  |  | 104.9 | 4.7 | 600 | 1.8 | 100.5 | 6.9 | 900 | 2.5 |  |  |  |  | 96.3 | 9 | 1200 | 3.3 | 92.3 | 11 | 1500 | 4 |  |  |  |  | 101.6 | 2.03 | 1520
Strainer |  |  | Medium Steel Pipe | 125 | [10 empty] | 900 | [17 empty] | 127 | 2.03 | 1210
Heat meter |  |  | P.V.C (Class 12) | 150 |  |  |  |  | 154.5 | 6.9 | 600 | 3.8 | 148.1 | 10.1 | 900 | 5.4 |  |  |  |  | 141.9 | 13.2 | 1200 | 7 | 135.9 | 16.2 | 1500 | 8.4 |  |  |  |  | 152.4 | 2.64 | 1310
|  |  | Stand WT Steel | 200 | 205.5 | 6.8 | 450 | 4.9 | 201.2 | 9 | 600 | 6.4 | 192.9 | 13.1 | 900 | 9.2 |  |  |  |  | 184.8 | 17.2 | 1200 | 11.8 | 177.1 | 21 | 1500 | 14.2 |  |  |  |  | 203.2 | 2.64 | 920
|  |  | Stainless Steel | 250 | 238 | 6 | 450 | 5 | 234 | 7.9 | 600 | 6.6 |  |  |  |  | 224 | 12.7 | 1000 | 10.3 | 220 | 15 | 1200 | 12.1 | 213 | 18.5 | 1500 | 14.6
|  |  |  | 300 | 300 | 7.5 | 450 | 7.8 | 295 | 9.8 | 600 | 10.2 |  |  |  |  | 283 | 16 | 1000 | 16.3 | 277 | 18.9 | 1200 | 19.1 | 268 | 23.3 | 1500 | 23.2
|  |  |  | 350 | 338 | 8.4 | 450 | 9.9 | 333 | 11.1 | 600 | 13 |  |  |  |  | 319 | 18 | 1000 | 20.6 | 312 | 21.3 | 1200 | 24.2 | 302 | 26.2 | 1500 | 29.4
|  |  |  | 400 | 381 | 9.4 | 450 | 12.6 | 375 | 12.4 | 600 | 16.4 |  |  |  |  | 360 | 20.2 | 1000 | 26.1 | 352 | 23.9 | 1200 | 30.7 | 341 | 29.5 | 1500 | 37.2
|  |  |  | 450 | 429 | 10.6 | 450 | 15.9 | 422 | 14 | 600 | 20.8 |  |  |  |  | 405 | 22.7 | 1000 | 33 | 396 | 27 | 1200 | 38.9 | 384 | 33.2 | 1500 | 47.1
|  |  |  | 500 | 476 | 11.8 | 450 | 19.6 | 469 | 15.5 | 600 | 25.5 |  |  |  |  | 450 | 25.2 | 1000 | 40.7
|  |  |  | 550 | 534 | 13.1 | 450 | 24.5 | 525 | 17.4 | 600 | 32.1
|  |  |  | 600 | 601 | 14.7 | 450 | 30.8 | 591 | 19.5 | 600 | 40.4
[5 empty] | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness