## summary
Serial no. | Material Description | U Btu/(hr)(oF)(ft2) | Weight Lb/ft2
1 | (Ext) 8" HCB with 3/4"plaster each side | 0.107 | 0
2 | (Ext) 6" HCB with 3/4"plaster each side | 0.467 | 45
3 | (Ext) 8" HCB with 3/4"plaster outside, and 1.2" polystyrene, 0.8" gypsum board inside(Placo board) | 0.112 | 51.47
4 | (Ext) 6" HCB with 3/4"plaster outside, and 1.2" polystyrene, 0.8" gypsum board inside(Placo board) | 0.115 | 41.3
5 | (Ext) 8" HCB with 1.2" mortar, 3/4" marble outside, and 1.2" polystyrene, 0.8" gypsum board inside (Placo board) | 0.111 | 60.2
6 | (Ext) 6" HCB with 1.2" mortar, 3/4" marble outside, and 1.2" polystyrene, 0.8" gypsum board inside (Placo board) | 0.113 | 50.03
7 | (Ext) 8" concrete with 3/4"plaster each side | 0.535 | 107.83
8 | (Ext) 6" concrete with 3/4"plaster each side | 0.585 | 84.5
9 | (Ext) 8" concrete with 3/4"plaster outside, and 1.2" polystyrene, 0.8" gypsum board inside(Placo board) | 0.119 | 104.13
10 | (Ext) 6" concrete with 3/4"plaster outside, and 1.2" polystyrene, 0.8" gypsum board inside(Placo board) | 0.121 | 80.8
11 | (Ext) 8" concrete with 1.2" mortar, 3/4" marble outside, and 1.2" polystyrene, 0.8" gypsum board inside (Placo) | 0.117 | 112.86
12 | (Ext) 6" concrete with 1.2" mortar, 3/4" marble outside, and 1.2" polystyrene, 0.8" gypsum board inside (Placo) | 0.119 | 89.53
13 | (Ext) double 6" HCB with 2" polysterene in between, and 3/4"plaster each side (sandwich wall) | 0.077 | 75.87
14 | (Ext) double 6" HCB with 2" air-gap in between, and 3/4"plaster each side (sandwich wall) | 0.255 | 75.5
15 | (Ext) double 6" HCB with 2" polyst. in between,1.2" mortar & 3/4" marble outside, and 3/4"plst inside (sandwich wall) | 0.076 | 84.6
16 | (Ext) double 6" HCB with 2" air-gap in between,1.2" mortar & 3/4" marble outside, and 3/4"plst inside (sandwich wall) | 0.246 | 84.23
17 | (Int) 4"HCB with 3/4" plaster each side | 0.515 | 34.83
18 | (Int) 6"HCB with 3/4" plaster each side | 0.389 | 45
19 | (Int) 8"HCB with 3/4" plaster each side | 0.361 | 55.17
20 | (Int) 4" concrete with 3/4"plaster each side | 0.505 | 61.17
21 | (Int) 6" concrete with 3/4"plaster each side | 0.467 | 84.5
22 | (Int) 8" concrete with 3/4"plaster each side | 0.435 | 107.83
23 | (Int) double 1/2"Gypsum wallboard partition with 3.5"air-gap | 0.305 | 5.69
24 | (Int) double 4" HCB with 2" air-gap in between, and 3/4"plaster each side (sandwich wall) | 0.253 | 55.16
25 | (Int) double 6" HCB with 2" air-gap in between, and 3/4"plaster each side (sandwich wall) | 0.23 | 75.5
26 | (Int) double 4" concrete with 2" air-gap in between, and 3/4"plaster each side (sandwich wall) | 0.316 | 107.84
27 | (Int) double 6" concrete with 2" air-gap in between, and 3/4"plaster each side (sandwich wall) | 0.287 | 154.5
28 | (ceiling) 1"terrazo, 1"mortar, 2"sand, 2.4"concrete, 5.6"hordi concrete blocks,and 3/4"internal plaster | 0.303 | 108.98
29 | (ceiling) 1"terrazo, 1"mortar, 2"sand, 8" solid slab concrete, and 3/4"internal plaster | 0.326 | 116.08
30 | (floor) 1"terrazo, 1"mortar, 2"sand, 2.4"concrete, 5.6"hordi concrete blocks, and 3/4"internal plaster | 0.373 | 108.98
31 | (floor) 1"terrazo, 1"mortar, 2"sand, 8" solid slab concrete, and 3/4"internal plaster | 0.408 | 116.08
32 | (roof) 0.8"screed, 2"polysterene, water proofing, 2.4" concrete, 5.6" hordi concrete blocks, 3/4"internal plastering | 0.081 | 82.25
33 | (roof) 0.8"screed, 2"polysterene, water proofing, 8"concrete,and 3/4" internal plastering | 0.083 | 108.68
34 | unshaded single exterior clear glass | 1.04 | -
35 | unshaded insulated double 1/4" glass, with 1/2" air-gap | 0.56 | -
36 | unshaded insulated triple 1/4" glass, with 1/4" air-gaps | 0.44 | -

## (1) Ext 8" HCB w-plst
overall heat transmission coefficient "U" for Wall
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | Pre-fabricated curtain type walls | 4 |  |  | 8.4 | 0
3 | Non-reflective air space |  | - | 61 |  | 0
4 | glass |  |  |  |  | 0
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 9.33
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.107
|  |  | Total weight Lb/ft2 = |  | 0

## (2) Ext 6" HCB w-plst
S.no. | Material Description | Th. (in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 2.14
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.467
|  |  | Total weight Lb/ft2 = |  | 45

## (3) Ext 8" HCB w-plst & placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 8 | - | 61 | 1.11 | 40.67
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
6 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.894
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.112
|  |  | Total weight Lb/ft2 = |  | 51.47

## (4) Ext 6" HCB w-plst & placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
6 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.694
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.115
|  |  | Total weight Lb/ft2 = |  | 41.3

## (5) Ext 8"HCB w-marble & placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | hollow concrete block | 8 | - | 61 | 1.11 | 40.67
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 9.044
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.111
|  |  | Total weight Lb/ft2 = |  | 60.2

## (6)Ext 6"HCB w-marble & placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.844
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.113
|  |  | Total weight Lb/ft2 = |  | 50.03

## (7)Ext 8"conc. w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand and gravel) | 8 | 0.08 | 140 | 0.64 | 93.33
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 1.87
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.535
|  |  | Total weight Lb/ft2 = |  | 107.83

## (8)Ext 6"conc. w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand and gravel) | 6 | 0.08 | 140 | 0.48 | 70
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 1.71
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.585
|  |  | Total weight Lb/ft2 = |  | 84.5

## (9)Ext 8"conc. w-plst &placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand &gravel) | 8 | 0.08 | 140 | 0.64 | 93.33
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
6 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.424
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.119
|  |  | Total weight Lb/ft2 = |  | 104.13

## (10)Ext 6"conc. w-plst & placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand &gravel) | 6 | 0.08 | 140 | 0.48 | 70
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
6 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.264
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.121
|  |  | Total weight Lb/ft2 = |  | 80.8

## (11)Ext 8"conc. w-marble &placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | concrete (sand & gravel) | 8 | 0.08 | 140 | 0.64 | 93.33
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.574
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.117
|  |  | Total weight Lb/ft2 = |  | 112.86

## (12)Ext 6"conc. w-marble &placo
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | concrete (sand & gravel) | 6 | 0.08 | 140 | 0.48 | 70
4 | polystyrene, smooth suface,(density 2.2) | 1.2 | 5 | 2.2 | 6 | 0.22
5 | Gypsum board (density 50) | 0.8 | 0.88 | 50 | 0.704 | 3.33
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 8.414
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.119
|  |  | Total weight Lb/ft2 = |  | 89.53

## (13) Ext double 6" HCB w-ins.
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | polystyrene, smooth suface,(density 2.2) | 2 | 5 | 2.2 | 10 | 0.37
5 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 13.05
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.077
|  |  | Total weight Lb/ft2 = |  | 75.87

## (14) Ext double 6" HCB w-airgap
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | nonreflective air space | 2 | - | - | 0.865 | -
5 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 3.915
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.255
|  |  | Total weight Lb/ft2 = |  | 75.5

## (15)sandw. wall w-ins. &marble
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
5 | polystyrene, smooth suface,(density 2.2) | 2 | 5 | 2.2 | 10 | 0.37
6 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
7 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
8 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 13.2
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.076
|  |  | Total weight Lb/ft2 = |  | 84.6

## (16)sandw. wall w-air. &marble
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | marble (like terrazo) | 0.75 | 0.08 | 70 | 0.06 | 4.38
3 | mortar | 1.2 | 0.2 | 116 | 0.24 | 11.6
4 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
5 | nonreflective air space | 2 | - | - | 0.865 | -
6 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
7 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
8 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 4.065
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.246
|  |  | Total weight Lb/ft2 = |  | 84.23

## (17)Int 4"HCB w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film (moving air, vertical) | - | - | - | 0.25 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 4 | - | 61 | 0.71 | 20.33
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 1.94
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.515
|  |  | Total weight Lb/ft2 = |  | 34.83

## (18)Int 6"HCB w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 2.57
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.389
|  |  | Total weight Lb/ft2 = |  | 45

## (19)Int 8"HCB w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 8 | - | 61 | 1.11 | 40.67
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 2.77
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.361
|  |  | Total weight Lb/ft2 = |  | 55.17

## (20)Int 4"con. w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand and gravel) | 4 | 0.08 | 140 | 0.32 | 46.67
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 1.98
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.505
|  |  | Total weight Lb/ft2 = |  | 61.17

## (21)Int 6"con. w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand and gravel) | 6 | 0.08 | 140 | 0.48 | 70
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 2.14
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.467
|  |  | Total weight Lb/ft2 = |  | 84.5

## (22)Int 8"con. w-plst
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete (sand and gravel) | 8 | 0.08 | 140 | 0.64 | 93.33
4 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
5 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 2.3
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.435
|  |  | Total weight Lb/ft2 = |  | 107.83

## (23)Int gyps. part.
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu |  | Weight - Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | 0.68 | - | -
2 | gypsum wallboard | 0.5 | - | 50 | 0.45 | 0.45 | 2.08 | 2.08
3 | (framing) nominal 2"x 4" wood stud | 3.5 | - | 32 | - | 4.38 | - | 15.33
4 | nonreflective air space | 3.5 | - | - | 0.85 | - | - | -
5 | gypsum wallboard | 0.5 | - | 50 | 0.45 | 0.45 | 2.08 | 2.08
6 | inside air film(still air, vertical) | - | - | - | 0.68 | 0.68 | - | -
|  |  |  | R = | 3.11 | 6.64 | 4.16 | 19.49
|  | U -Btu/(hr)(oF)(ft2) = |  |  | 0.322 | 0.151 | Bet. framing | At framing
[5 empty] | Bet. framing | At framing
| with 10% framing, Uav=0.9(0.322) + 0.1(0.151) = |  |  |  | 0.305
| with 10% framing, WTav=0.9(4.16) + 0.1(19.49) = |  |  |  | 5.69

## (24) Int double 4" HCB w-airgap
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 4 | - | 61 | 0.71 | 20.33
4 | nonreflective air space | 2 | - | - | 0.865 | -
5 | hollow concrete block | 4 | - | 61 | 0.71 | 20.33
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 3.945
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.253
|  |  | Total weight Lb/ft2 = |  | 55.16

## (25) Int double 6" HCB w-airgap
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
4 | nonreflective air space | 2 | - | - | 0.865 | -
5 | hollow concrete block | 6 | - | 61 | 0.91 | 30.5
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 4.345
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.23
|  |  | Total weight Lb/ft2 = |  | 75.5

## (26) Int double 4" con w-airgap
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete(sand & gravel) | 4 | 0.08 | 140 | 0.32 | 46.67
4 | nonreflective air space | 2 | - | - | 0.865 | -
5 | concrete(sand & gravel) | 4 | 0.08 | 140 | 0.32 | 46.67
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 3.165
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.316
|  |  | Total weight Lb/ft2 = |  | 107.84

## (27) Int double 6" con w-aigap
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, vertical) | - | - | - | 0.68 | -
2 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
3 | concrete(sand & gravel) | 6 | 0.08 | 140 | 0.48 | 70
4 | nonreflective air space | 2 | - | - | 0.865 | -
5 | concrete(sand & gravel) | 6 | 0.08 | 140 | 0.48 | 70
6 | cement plaster, sand aggregate | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, vertical) | - | - | - | 0.68 | -
|  |  |  | R = | 3.485
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.287
|  |  | Total weight Lb/ft2 = |  | 154.5

## (28)hordi ceiling
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R- (hr)(oF)(ft2)/Btu |  | Weight - Lb/ft2
1 | inside air film(still air, horizontal) | - | - | - | 0.92 | 0.92 | - | -
2 | terrazo | 1 | 0.08 | 70 | 0.08 | 0.08 | 5.83 | 5.83
3 | mortar | 1 | 0.2 | 116 | 0.2 | 0.2 | 9.67 | 9.67
4 | sand | 2 | 0.08 | 116 | 0.16 | 0.16 | 19.33 | 19.33
5 | concrete | 2.4 | 0.08 | 140 | 0.192 | 0.192 | 28 | 28
6 | hordi concreteblocks | 5.6 | - | 61 | 0.78 | - | 28.47 | -
7 | concrete | 5.6 | 0.08 | 140 | - | 0.448 | - | 65.33
8 | plaster | 0.75 | 0.2 | 116 | 0.15 | 0.15 | 7.25 | 7.25
9 | inside air film(still air, horizontal) | - | - | - | 0.92 | 0.92 | - | -
|  |  |  | R = | 3.402 | 3.07 | 98.55 | 135.41
|  | U -Btu/(hr)(oF)(ft2) = |  |  | 0.294 | 0.326 | At hordi blocks | between hordis
[5 empty] | At hordi blocks | between hordis
|  | hordi block width= |  |  | 15.2
| conc. width between hordis= |  |  |  | 6
|  | Overall U -Btu/(hr)(oF)(ft2) = |  |  | 0.303
|  | total weight Lb/ft2 = |  |  | 108.98

## (29)solid slab ceiling
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, horizontal) | - | - | - | 0.92 | -
2 | terrazo | 1 | 0.08 | 70 | 0.08 | 5.83
3 | mortar | 1 | 0.2 | 116 | 0.2 | 9.67
4 | sand | 2 | 0.08 | 116 | 0.16 | -
5 | concrete | 8 | 0.08 | 140 | 0.64 | 93.33
6 | plaster | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, horizontal) | - | - | - | 0.92 | -
|  |  |  | R = | 3.07
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.326
|  |  | Total weight Lb/ft2 = |  | 116.08

## (30)hordi floor
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R- (hr)(oF)(ft2)/Btu |  | Weight - Lb/ft2
1 | inside air film(still air, horizontal) | - | - | - | 0.61 | 0.61 | - | -
2 | terrazo | 1 | 0.08 | 70 | 0.08 | 0.08 | 5.83 | 5.83
3 | mortar | 1 | 0.2 | 116 | 0.2 | 0.2 | 9.67 | 9.67
4 | sand | 2 | 0.08 | 116 | 0.16 | 0.16 | 19.33 | 19.33
5 | concrete | 2.4 | 0.08 | 140 | 0.192 | 0.192 | 28 | 28
6 | hordi concrete blocks | 5.6 | - | 61 | 0.78 | - | 28.47 | -
7 | concrete | 5.6 | 0.08 | 140 | - | 0.448 | - | 65.33
8 | plaster | 0.75 | 0.2 | 116 | 0.15 | 0.15 | 7.25 | 7.25
9 | inside air film(still air, horizontal) | - | - | - | 0.61 | 0.61 | - | -
|  |  |  | R = | 2.782 | 2.45 | 98.55 | 135.41
|  | U -Btu/(hr)(oF)(ft2) = |  |  | 0.359 | 0.408 | At hordi blocks | between hordis
[5 empty] | At hordi blocks | between hordis
|  | hordi block width= |  |  | 15.2
| conc. width between hordis= |  |  |  | 6
|  | Overall U -Btu/(hr)(oF)(ft2) = |  |  | 0.373
|  | total weight Lb/ft2 = |  |  | 108.98

## (31)solid slab floor
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | inside air film(still air, horizontal) | - | - | - | 0.61 | -
2 | terrazo | 1 | 0.08 | 70 | 0.08 | 5.83
3 | mortar | 1 | 0.2 | 116 | 0.2 | 9.67
4 | sand | 2 | 0.08 | 116 | 0.16 | -
5 | concrete | 8 | 0.08 | 140 | 0.64 | 93.33
6 | plaster | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, horizontal) | - | - | - | 0.61 | -
|  |  |  | R = | 2.45
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.408
|  |  | Total weight Lb/ft2 = |  | 116.08

## (32)hordi insulated roof
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R- (hr)(oF)(ft2)/Btu |  | Weight - Lb/ft2
1 | outside air film(moving air, horizontal) | - | - | - | 0.25 | 0.25 | - | -
2 | screed | 0.8 | 0.2 | 116 | 0.16 | 0.16 | 7.73 | 7.73
3 | polystyrene, smooth suface,(density 2.2) | 2 | 5 | 2.2 | 10 | 10 | 0.37 | 0.37
4 | water proofing & paints | - | - | - | - | - | - | -
5 | concrete | 2.4 | 0.08 | 140 | 0.192 | 0.192 | 28 | 28
6 | hordi concrete blocks | 5.6 | - | 61 | 0.78 | - | 28.47 | -
7 | concrete | 5.6 | 0.08 | 140 | - | 0.448 | - | 65.33
8 | plaster | 0.75 | 0.2 | 116 | 0.15 | 0.15 | 7.25 | 7.25
9 | inside air film(still air, horizontal) | - | - | - | 0.92 | 0.92 | - | -
|  |  |  | R = | 12.452 | 12.12 | 71.82 | 108.68
|  | U -Btu/(hr)(oF)(ft2) = |  |  | 0.08 | 0.083 | At hordi blocks | between hordis
[5 empty] | At hordi blocks | between hordis
|  | hordi block width= |  |  | 15.2
| conc. width between hordis= |  |  |  | 6
|  | Overall U -Btu/(hr)(oF)(ft2) = |  |  | 0.081
|  | total weight Lb/ft2 = |  |  | 82.25

## (33)concrete insulated roof
S.no. | Material Description | Th.(in.) | Res./in | Density Lb/ft3 | R (hr)(oF)(ft2)/Btu | Weight Lb/ft2
1 | outside air film(moving air, horizontal) | - | - | - | 0.25 | -
2 | screed | 0.8 | 0.2 | 116 | 0.16 | 7.73
3 | polystyrene, smooth suface,(density 2.2) | 2 | 5 | 2.2 | 10 | 0.37
4 | water proofing & paints | - | - | - | - | -
5 | concrete | 8 | 0.08 | 140 | 0.64 | 93.33
6 | plaster | 0.75 | 0.2 | 116 | 0.15 | 7.25
7 | inside air film(still air, horizontal) | - | - | - | 0.92 | -
|  |  |  | R = | 12.12
|  |  | U -Btu/(hr)(oF)(ft2) = |  | 0.083
|  |  | Total weight Lb/ft2 = |  | 108.68