## Temp (hidden)
40
140
60
4.44

## StorageFact (hidden)
1.25

## DemandFact (hidden)
0.3

## Main
|  |  |  | Project No. |  | Date
|  |  |  | Sheet No. |  | Computed by
|  |  |  | 1 | 1
Subject | Electric Water heater calcularion |  |  | Checked by |  | Approved by
| Application Type | Office Building |  | 8
Qty | Fixtures Selected | [6 empty] | 0
| Bathtubs | * | 0 | gph | = | 0 | gph | 0
| Kitchen Sinks | * | 20 | gph | = | 0 | gph | 0
| Private Lavatory | * | 2 | gph | = | 0 | gph | 0
4 | Public Lavatory | * | 6 | gph | = | 24 | gph | 24
1 | Showers | * | 30 | gph | = | 30 | gph | 54
54
54
|  | CALCULATION RESULTS | [5 empty] | 54
54
|  | Possible Maximum Demand: |  |  |  | 54 | gph | 108
108
| Demand Factor: | Demand Factor: |  | 0.3 | 0.3 |  |  | 108
108
|  | Probable Maximum Demand: |  |  |  | 16.2 | gph | 124.2
124.2
|  | Heater Recovery Capacity: |  |  |  | 16.2 | gph | 140.4
140.4
| Storage Factor: | Storage Factor: |  | 2 | 2 |  |  | 140.4
|  | Strorage Tank Capacity: |  |  |  | 32.4 | gal
Hot Water Tank Inlet / Outlet Temperatures:
|  | T in (Deg F): | 40
|  | T out (Deg F): | 140
|  | Heater or Coil Capacity: |  | 13500 | Btu/hr
|  |  |  | 3.9566 | KW
of

## Data
| Apartement House | Club | Gymnasium | Hospital | Hotel | Industrial Plant | Office Building | Private Residence | School | Y.M.C.A
Private lavatory | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Public lavatory | 4 | 6 | 8 | 6 | 8 | 12 | 6 |  | 15 | 8
Bathtubs | 20 | 20 | 30 | 20 | 20 |  |  | 20 |  | 30
Dishwashers | 15 | 100 |  | 100 | 100 | 60 |  | 15 | 60 | 60
Foot Basins | 3 | 3 | 12 | 3 | 3 | 12 |  | 3 | 3 | 12
Kitchen Sinks | 10 | 20 |  | 20 | 30 | 20 | 20 | 10 | 20 | 20
Laundry Tubs | 20 | 28 |  | 28 | 28 |  |  | 20 |  | 28
Pantry Sinks | 5 | 10 |  | 10 | 10 |  | 10 | 5 | 10 | 10
Showers | 30 | 150 | 225 | 75 | 75 | 225 | 30 | 30 | 225 | 225
Slop Sink | 20 | 20 |  | 20 | 30 | 20 | 20 | 15 | 20 | 20
Hydrotherapeutic Showers |  |  |  | 400
Hubbard Baths |  |  |  | 600
Leg Baths |  |  |  | 100
Arm Baths |  |  |  | 35
Sitz Baths |  |  |  | 30
Continous Flow Baths |  |  |  | 165
Circular Wash Sinks |  |  |  | 20 | 20 | 30 | 20 |  | 30
Semicircular Wash Sinks |  |  |  | 10 | 10 | 15 | 10 |  | 15
Demand Factor: | 0.3 | 0.3 | 0.4 | 0.25 | 0.25 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4
Storage Factor: | 1.25 | 0.9 | 1 | 0.6 | 0.8 | 1 | 2 | 0.7 | 1 | 1
Apartment House | 2
Club | 3
Gymnasium | 4
Hospital | 5
Hotel | 6
Industrial Plant | 7
Office Building | 8
Private Residence | 9
School | 10
Y.M.C.A | 11