## Sheet1
Evaporative Cooler Sizing Calculator Sheet
Design Temperatures
| Outside dry bulb temp. (DBT) |  | 115 | F
| Outside wet bulb temp. (WBT) |  | 68 | F
| Inside dry bulb temp. (T) |  | 84 | F
| Total sensible heat gain |  | 36000 | BTU
| Media Saturation Efficiency (Eff.) |  | 0.85
| Leaving Air DBT = | DB - [( DB - WB ) * Eff.] | 75.05 | F
| Air Flow = | Sensible heat gain | 3724.3948 | CFM
1.08 ( T - LDBT )