## Sheet1
RAIN WATER DRAINAGE DESIGN CALCULATION
1- calculate the total area of roof
2- determine the maximum hourly rainfall in inches .
3 - select leader size (3,4,5,6,inch)
4- from table 1 determine the area can be drained by leader at max. rainfall rate.
5-divide the total roof area by the area can be drained by leader at max. rainfall rate.
ROOF DRAIN VERTICAL LEADER REQUIREMENTS FOR HORIZONTAL ROOF AREAS AT VARIOUS RAINFALL RATES
Leaders pipe size inches | size open area sq.in. | Hourly Rain Fall In Inches
|  | 1 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8
2 | 3.14 | 2880 | 1920 | 1440 | 1150 | 960 | 720 | 575 | 480 | 410 | 360
3 | 7.06 | 8880 | 5860 | 4400 | 3520 | 2930 | 2200 | 1760 | 1470 | 1260 | 1100
4 | 12.56 | 18400 | 12700 | 9200 | 7360 | 6130 | 4600 | 3680 | 3070 | 2630 | 2300
5 | 19.6 | 34600 | 23050 | 17300 | 13840 | 11530 | 8650 | 6920 | 5765 | 4945 | 4325
6 | 28.3 | 54000 | 36000 | 27000 | 21600 | 18000 | 13500 | 10800 | 9000 | 7715 | 6750
8 | 50.25 | 116000 | 77400 | 58000 | 46400 | 38680 | 29000 | 23200 | 19315 | 16570 | 14500
TABLE 1
ALLOWABLE FLOW FOR VERTICAL LEADERS AND HORIZONTAL STORM DRAINS
ALLOWABLE FLOW IN GPM
PIPE SIZE |  | VERTICAL LEADER |  |  | HORIZONTAL STORM DRAINS SLOPE PER FOOT
[5 empty] | 1/8" |  | 1/4" |  | 1/2"
2 |  | 30 |  |  | 12 |  | 17 |  | 24
3 |  | 90 |  |  | 36 |  | 51 |  | 72
4 |  | 192 |  |  | 78 |  | 111 |  | 157
5 |  | 348 |  |  | 142 |  | 201 |  | 284
6 |  | 566 |  |  | 231 |  | 327 |  | 462
8 |  | 1220 |  |  | 498 |  | 705 |  | 996
10 |  | 2200 |  |  | 902 |  | 1275 |  | 1804
12 |  | #VALUE! |  |  | 1467 |  | 2076 |  | 2934
15 |  | 0 |  |  | 2666 |  | 3774 |  | 5332
TABLE 2
STEPS FOR CALCULATING DRAINAGE REQUIREMENTS USING GPM
GPM = 0.0104 *R*A
R = RAINFALL INTENSITY- INCHES/HOUR = 4"
A = ROOF AREA - SQUARE FEET = 135000
GPM = 0.0104 *4*135000 = 5613 =5620
REFER TO TABLE 2 A4' LEADER WILL HANDLE 192 GPM
5616 ÷192 = 29.25 =30 a 4" leaders rerquired
5616 ÷566 =9.9 = 10 a6" leader
| 0.0104 | A | R | GPM | 3" | 4" | 5" | 6" | No.of3" | No. 4" | No.5"
| 0.0104 | 135000 | 4 | 5616 | 90 | 192 | 348 | 566 | 63 | 30 | 17