## Water & Drainage
WATER DEMAND & DRAINAGE FLOW
Project No.: |  |  | Date: |  | Sheet No.: | 1 of | 1 | Computed by:
Location : | [7 empty] | Checked by:
Building: | [7 empty] | Approved by:
| WATER DEMAND | [6 empty] | DRAINAGE
| Fixture Type |  |  | Weight in FU | QTY. | Total FU |  | Weight in FU | QTY. | Total FU
| Water Closet, Flush Valve Public |  |  | 10 | 33 | 330 |  | 8 | 33 | 264
| Water Closet, Flush Tank Public |  |  | 5 | 9 | 45 |  | 4 | 9 | 36
| Water Closet, Flush Tank Private |  |  | 3 | 2 | 6 |  | 4 | 2 | 8
| Stall or Wall Urinal, Flush Valve |  |  | 10 | 4 | 40 |  | 4 | 4 | 16
| Lavatory, Faucet, Public |  |  | 2 | 48 | 96 |  | 2 | 48 | 96
| Lavatory, Faucet, Private |  |  | 1 | 2 | 2 |  | 1 | 2 | 2
| Shower Head, Public |  |  | 4 | 14 | 56 |  | 3 | 14 | 42
| Shower Head, Private |  |  | 2 | 2 | 4 |  | 2 | 2 | 4
| Cafeteria Kitchen Sink, Faucet |  |  | 4 | 3 | 12 |  | 3 | 3 | 9
| Utility Sink (Pantry), Faucet, Public |  |  | 3 | 7 | 21 |  | 3 | 7 | 21
| Double Sink (Pantry), Faucet, Public |  |  | 3 | 2 | 6 |  | 3 | 2 | 6
| Mop Sink, Faucet, Public |  |  | 3 | 4 | 12 |  | 3 | 4 | 12
| Water Cooler |  |  | 0.5 | 4 | 2 |  | 0.5 | 4 | 2
| Water Taps |  |  | 1 | 20 | 20 | FD | 1 | 20 | 20
| Ablution Water Taps |  |  | 2 | 18 | 36 | Ablution FD | 1 | 18 | 18
| Pre-Rinse Spray Unit |  |  | - | 2 | - |  | - | 2 | -
| Dishwasher |  |  | 3 | 2 | 6 |  | 2 | 2 | 4
| BPH (Only With Flush Tank WC) |  |  | 1 | 11 | 11 |  | - | 11 | -
| Eye Wash |  |  | 2 | 2 | 4 |  | - | 2 | -
| Water Connection to Expansion Tank |  |  | 15 | 1 | 15 |  | - | 1 | -
|  | TOTAL |  |  |  | 724 |  |  |  | 560
* For Supply outlets which impose a continuous demand, estimate demand and add to the total demand, after reference to the curve
* Given Weights are for total demand. For fixtures with both hot and cold water supplies, the weight for maximum separate demand
may be taken as 3/4 of the listed demand for the supply

## Water Requirement
WATER DEMAND CALCULATION
Project no.: |  |  | Date: |  | Sheet No.: | 1 of | 1 |  |  |  | Computed by:
Location : | [10 empty] | Checked by:
Building: | Office/Warehouse | [9 empty] | Approved by:
|  |  |  | Office Bldg |  |  |  |  | Warehouse |  |  | Summary of Results
Weight in FU | Fixture Type |  |  | Basement | Ground Floor | First Floor | Second Floor | Roof | Ground | First | Second | Total | Total Weight in FU
10 | Water Closet, Flush Valve Public |  |  | - | 6 | 8 | 8 | - | 11 | - | - | 33 | 330
5 | Water Closet, Flush Tank Public |  |  | - | 4 | 1 | 2 | - | - | 2 | - | 9 | 45
3 | Water Closet, Flush Tank Private |  |  | - | - | - | 2 | - | - | - | - | 2 | 6
10 | Stall or Wall Urinal, Flush Valve |  |  | - | - | 2 | 2 | - | - | - | - | 4 | 40
2 | Lavatory, Faucet, Public |  |  | - | 12 | 11 | 12 | - | 11 | 2 | - | 48 | 96
1 | Lavatory, Faucet, Private |  |  | - | - | - | 2 | - | - | - | - | 2 | 2
4 | Shower Head, Public |  |  | - | 2 | - | - | - | 12 | - | - | 14 | 56
2 | Shower Head, Private |  |  | - | - | - | 2 | - | - | - | - | 2 | 4
4 | Cafeteria Kitchen Sink, Faucet |  |  | - | 3 | - | - | - | - | - | - | 3 | 12
3 | Utility Sink (Pantry), Faucet, Public |  |  | - | 1 | 2 | 3 | - | - | 1 | - | 7 | 21
3 | Double Sink (Pantry), Faucet, Public |  |  | - | - | 1 | 1 | - | - | - | - | 2 | 6
3 | Mop Sink, Faucet, Public |  |  | - | 2 | 1 | 1 | - | - | - | - | 4 | 12
0.5 | Water Cooler |  |  | - | - | 2 | 2 | - | - | - | - | 4 | 2
1 | Water Tap |  |  | 1 | 2 | - | - | 3 | 8 | 2 | 4 | 20 | 20
2 | Ablution Water Tap |  |  | - | 10 | 4 | 4 | - | - | - | - | 18 | 36
- | Pre-Rinse Spray Unit |  |  | - | 2 | - | - | - | - | - | - | 2
3 | Dishwasher |  |  | - | 2 | - | - | - | - | - | - | 2 | 6
1 | BPH (Only With Flush Tank WC) |  |  | - | 4 | 1 | 4 | - | - | 2 | - | 11 | 11
2 | Eye Wash |  |  | - | - | - | - | - | 1 | - | - | 1 | 2
15 | Water Connection to Expansion Tank |  |  | - | - | - | - | 1 | - | - | - | 1 | 15
[11 empty] | Total | 189 | 722
FU
| Drivers Rm |  | 54
| Generator Rm |  | 3
| Mussallah |  | 26 | or Take | 1 l/s
| Total FU | 802
| GPM | 186 | *With Flush Valve
| L/s | 11.7
|  |  | Tank capacity (Liters) |  | Flow for 1.5 hours filling (l/s)
| Mussallah |  | 5000 |  | 0.92593 | 14.6759 | GPM

## Vessel & Head Calculation
Pressurizing Vessel & Head Calculation
Project no.: |  | Date: | Sheet No.: | 1 of | 1 | Computed by:
Location : | [5 empty] | Checked by:
Building: | [5 empty] | Approved by:
Pressurizing Vessel
V= 16.5* (Q / Zmax ) * (Pu*Pi) / (DP*Pc)
V= total tank volume in L.
Q= flow of the pump = 690 l/min.
Zmax = maximum number of start /stops = 12.
| Pu = absolute cut out pressure = 6+1 = 7 bars. |  |  | Volume= | 2530 | liters
| Pi = absolute cut in pressure = 3+1 = 4 bars. |  |  | * Since the Pump is Variable Speed the Vessel required is only 500 L
| DP = Pu - Pi. |  |  | * to determine The volume of a pressurizing tank connected to several pumps of same
| Pc = initial air charge. Pc=Pi-0.5=3.5 bars. |  |  | characteristics use the average flow of one pump and the lowest cut in and cut out
| Utilizable water volume between pump start and pump stop: |  |  | corresponding to the last pump.(Several cut in cut out pressure should show on the schedule.
DV=16.5*Q/Zmax = 16.5*690/12= 950 L
Pressure Head Calculation
Office Bldg
| Required Residual Pressure at FV EWC |  | 14 | m
| Static Head |  | 14 | m
| Longuest Run |  | 140
| Safety factor |  | 1.25
| Equivalent Run |  | 175
| Friction rate |  | 5 psi/100 ft | if | 5%
| Friction Loss |  | 19.7931 | m | 8.75 | m
| Total Head |  | 47.7931 | m | 36.75 | m | * Need to be Corrected on Dwgs
Warehouse
| Required Residual Pressure at WT |  | 4 | m | FV EWC is not counted because it is not the most remoted
| Static Head |  | 16 | m | It is going up then dn
| Longuest Run |  | 200
| Safety factor |  | 1.25
| Equivalent Run |  | 250
| Friction rate |  | 5 psi/100 ft | if | 5%
| Friction Loss |  | 28.2759 | m | 12.5 | m
| Total Head |  | 48.2759 | m | 32.5 | m
* to determine The volume of a pressurizing tank connected to several pumps of same
characteristics use the average flow of one pump and the lowest cut in and cut out
corresponding to the last pump.(Several cut in cut out pressure should show on the schedule.
* Since the pumps are alternating the number of Start/Stop will be taken twice that of one pump
The number of start stop of one pump may be taken max=30 (for small pumps) and min 10-12
* Pc can be increased but should not exceed Pi
* Around 6 Start/Stop if the pump is higher than 50 KW
* Around 15 Start/Stop if the pump is from 30 KW to 50 KW
* Max 25 Start/Stop if the pump is lower than 30 KW
* refer to sheet in J0520-2 Project
* For open system use 5psi/100ft friction

## Fixtures Req'rd Pressure
Fixtures Flows and Pressures
Project no.: |  | Date: |  | Sheet No.: | 1 of | 1 | Computed by:
Location : | [6 empty] | Checked by:
Building: | [6 empty] | Approved by:
|  | Flow Pressure PSI | Flow Pressure m | Flow Rate GPM | Flow Rate L/S
| Ordinary Basin Faucet | 8 | 5.6 | 3 | 0.2
| Self Closing Basin Faucet | 12 | 8.4 | 2.5 | 0.2
| Sink Faucet, 3/8 in | 10 | 7 | 4.5 | 0.3
| Sink Faucet, 1/8 in | 5 | 3.5 | 4.5 | 0.3
| Bathtub Faucet | 5 | 3.5 | 6 | 0.4
| Laundry Tub Cock, 1/2 in. | 5 | 3.5 | 5 | 0.4
| Shower | 12 | 8.4 | 5 | 0.4
| Ball Cock For Closet | 15 | 10.5 | 3 | 0.2
| Flush Valve For Closet | 15 to 20 | 10.5 to 14 | 15 to 40 | 1 to 2.5
| Flush Valve For Urinal | 15 | 10.5 | 15 | 1
| Garden Hose, 50ft, and Sill Cock | 30 | 21 | 5 | 0.4
* 1m= 1.45 psi
1 bar=14.50377 psi
1 bar = 100kPa