## Cold Storage Design
REFRIGERATED COLD STORAGE DESIGN
Refrigeration Requuirements:
Given: | Fruits and Vegetables |  | Specific Heat, Hs: |  | 3.8 | KJ
| Storage Temperature: |  | From 21º to 0ºC |  | 21 | ºC
| Store Room Dimension: |  | 3X3X3 | m³ | 31.5 | cu.m.
| Store Room Height: |  |  |  | 3 | m
| Crate Dimension: |  | 37x53x31 | cm³ | 0.060791 | cm³
| Store Room Capacity:Crates |  |  |  | 415 | Crates
| Weight of fruits per crate: |  |  |  | 20 | kgs.
| Total Capacity: |  | 8300 | kgs.
| Weight of the crate container: |  |  |  | 2 | kgs.
| Heat Loss, Walls: |  | Length | Width | 1.053 | KJ/sq.m.ºC-hr | R-value | 0.94967 | sq.m.ºC-hr/KJ
| Wall area, sq.m. |  | 3.5 | 3 | 39 | sq.m.
| Heat Loss, Floor: |  |  |  | 34.1 | KJ/h-sq.m. | R-value | 0.029326 | sq.m.-hr/KJ
| Floor Area, sq.m.: |  |  |  | 10.5 | sq.m.
| Ceilling Area, sq.m.: |  |  |  | 10.5 | sq.m.
| Heat Loss, Ceiling: |  |  |  | 0.635 | KJ/h-sq.m. | R-value | 1.5748 | sq.m.-hr/KJ
COMPUTATION: |  | Fruits and Vegetables
1 | HEAT LOAD = W*Hs*ºC |  |  | 662340 | KJ/day
|  |  |  | 27597.5 | KJ/hr
1.1 | POWER REQT. , Watts: |  |  | 7665.9722 | Watts
2 | HEAT LOAD, Crates: |  |  | 43575 | KJ/day
|  |  |  | 1815.625 | KJ/hr
3 | Respiration Heat Maximum:
| Heat Maximum of fruit |  |  | 8130.1958 | KJ/hr
on the seventh day storage
3.1 | Additional Respiration Heat: |  |  | 3285.4167 | KJ/hr
5 days intake of fruit cooled
to 0ºC
4 | Heat Transmission (Walls): |  |  | 862.407 | KJ/hr
5 | Heat Transmission (Floor): |  |  | 358.05 | KJ/hr
8ºC temperature Difference
6 | Heat Transmission (Ceiling): |  |  | 200.025 | KJ/hr
| Temperature Difference |  | 30 | ºC
7 | Electrical Heat Load:
| Lights | 40 | Watts | 2304 | KJ/hr
| No.of light | 2 | units
| Fan Motors | 1.5 | Hp | 4029 | KJ/hr
| No. of Fan | 1 | unit
8 | Air infiltration assumes three |  |  | 4252.5 | KJ/hr
complete air changes in 24 h,
outside air 21ºC
| 45 | KJ/cu.m.21ºC
TOTAL AMOUNT OF HEAT PER HOUR: |  |  |  | 52834.7195 | KJ/hr
| Power Requirement: Watts |  |  | 14.6763 | KWatts
| Compressor Power Reqt., Watts |  |  | 17.2662 | KWatts | 23.1451 | Hp
| Refrigeration Requirement, Tonnes |  |  | 4.1694 | tonnes
Note on F5: ====== ID#AAAAGk36pjw Buenaventura Pitao (2020-05-30 20:38:50) Enter data on yellow colored cells
Note on E15: ====== ID#AAAAGk36pkA Buenaventura Pitao (2020-05-30 20:38:50) Indicate wall dimension
Note on D44: ====== ID#AAAAGk36pj0 Buenaventura Pitao (2020-05-30 20:38:50) Indicate temperature difference from outside and inside room
Note on C48: ====== ID#AAAAGk36pjo Buenaventura Pitao (2020-05-30 20:38:50) Indicate wattage of light in the storage room (e.g. flourescent, incandescent)
Note on C49: ====== ID#AAAAGk36pj4 Buenaventura Pitao (2020-05-30 20:38:50) Indicate the number of lights
Note on C51: ====== ID#AAAAGk36pjs Buenaventura Pitao (2020-05-30 20:38:50) Indicate the fan motor HP
Note on C52: ====== ID#AAAAGk36pj8 Buenaventura Pitao (2020-05-30 20:38:50) Indicate the number of fan motor units
Note on B57: ====== ID#AAAAGk36pkE Buenaventura Pitao (2020-05-30 20:38:50) Indicate the air temperature changes from the outside

## Com. Respiration Heat
Commulative Respiration Heat of fruits during cooling
produced when a tonne of fruits are stored daily
Days from Start of Loading | Mean Fruit temperature (ºC)* | [6 empty] | TOTAL HEAT (KJ)
| 15 | 10 | 6 | 4 | 2 | 1 | 0
1 | 7000 | [6 empty] | 7000
2 | 7000 | 5217 | [5 empty] | 12217
3 | 7000 | 5217 | 2917 |  |  |  |  | 15134
4 | 7000 | 5217 | 2917 | 2009 |  |  |  | 17143
5 | 7000 | 5217 | 2917 | 2009 | 2344 |  |  | 19487
6 | 7000 | 5217 | 2917 | 2009 | 2344 | 2122 |  | 21609
7 | 7000 | 5217 | 2917 | 2009 | 2344 | 2122 | 1900 | 23509
* Approximate average temperature of the fruit during successive days as it is being cooled from 21ºC to 0ºC