## 1
Fire Pump Head Calculations Sheet
Project no: |  | Date: | 20-09-07 | Sheet No. | 1 | of | 2 | Computed by:
Subject: | Fire pump Head Calculation | [6 empty] | Checked by:
Approved by:
1- Abbreviations:
Hs | = | Static Head (m)
Hr | = | Residual Head (m)
HL | = | Friction Loss Head (m)
Q | = | Flow rate (gpm)
C | = | Hazen-Williams C value
d | = | Diameter of pipe (inches)
P | = | Frictional resistance (psi /ft of pipe)
2- Parameters:
Q1 | = | 1250 | gpm
Q2 | = | 750 | gpm
Q3 | = | 500 | gpm
d1 | = | 8 | inch
d2 | = | 6 | inch
d3 | = | 6 | inch
L1 | = | 50 | m
| = | 164.042 | ft
L2 | = | 90 | m
| = | 295.2756 | ft
L3 | = | 100 | m
| = | 328.084 | ft
C | = | 120 |  | (see NFPA13 - Table 22.4.4.7)
P | = | 4.52 * (Q)1.85/C1.85 * d4.87 |  | (see NFPA13 - Enc# 22.4.2.1.1)
3- Static Head:
Hs | = | 0 | m
| = | 0 | ft
4- Residual Pressure:
Hr | = | 6.9 | bar
| = | 230.8566 | ft
5- Friction Loss Head:
1- Friction Loss in Pipes:
P1 | = | 0.0138 | Psi/ ft
P2 | = | 0.021773 | Psi/ ft
P3 | = | 0.010284 | Psi/ ft
HL1 | = | 2.2638 | Psi
HL2 | = | 6.4291 | Psi
HL3 | = | 3.3739 | Psi
HLT | = | 12.0668 | Psi
| = | 0.83201 | bar
| = | 27.8369 | ft

## 2
Fire Pump Head Calculations Sheet
Project no: |  | Date: | 20-09-07 | Sheet No. | 1 | of | 2 | Computed by:
Subject: | Fire pump Head Calculation | [6 empty] | Checked by:
Approved by:
2- Friction Loss in Fittings and valves:
HLF | = | 5.5674 | ft | (20% of pipes)
6- Head of fire pump:
H | = | Hs + Hr + HLF + HLP
| = | 264.2608 | ft
| = | 80.5467 | m
| = | 7.8984 | bar
| = | 114.5527 | Psi
| H = | 120 |  | Psi