## Project Info Input
Installer company
FirePro®
Design Calculation Software
Fire Extinguishing Aerosol Systems
Distributor/Master Dealer:
Project Name:
Date:
Client's Name:
Clinent's Code:
Address:
Tel.:
Fax:
Email:
| Website: | www.firepro.info
Special Notes:
No Special Notes Required
Please start from Volume Calculation Sheet
FirePro Systems Ltd all rights reserved

## Volume 1 Calcs
Installer company
FirePro®
D e s i g n C a l c u l a t i o n S h e e t
[14 empty] | Meters |  | Class A - Combustible Solids / Electically Energized Fires
VOLUME 1 | [13 empty] | Feet |  | Class B - Combustible Liquids
Class C - Combustible Gases
SELECT UNITS | Meters | [14 empty] | Class F - Flammable Oil & Fats
VOLUME | 120.84 |  |  | 120.84
(if not to be calculated) | [13 empty] | m3 | ft3 |  | Rectangular | UP TO 0.6
[17 empty] | Triangular | 0.6<SL<2.5
ROOM NAME & No. | A/C Room | [15 empty] | Semi-Cylindrical | 2.5<SL<4.0
[17 empty] | Cylindrical | 4.0<SL<8.0
SPACE TYPE | Electrical Rooms <4m Height
ROOM SHAPE | Rectangular | [12 empty] | Computer Cubicle
| Length |  |  | Width |  |  | Height | [6 empty] | Electrical Panel/Cabinet
SECTION DIMENSION | 6 | m | x | 5.3 | m | x | 3.8 | m | = | VOLUME | = | 120.84 | m3 | Other Small Electrical Enclosure
Small Size Enclosure - Other
[7 empty] | 3.8 | [6 empty] | Raised Floor Enclosure
CLASS OF FIRE | Class A - Combustible Solids / Electically Energized Fires | [12 empty] | Suspended Ceiling Enclosure
Medium Size Enclosure - Other
STREAM REQUIRED (m) | 2.5<SL<4.0 |  |  | m | [9 empty] | Medium Size Boat Engine Compartment
Plant Room
SAFETY FACTOR (sf)** | 1.3 | [12 empty] | Telecom Room
Computer Room
**FOR ADDITIONAL SAFETY REPLACE CURRENT SAFETY FACTOR AS APPLICABLE | [13 empty] | Electrical Rooms <4m Height
Transformer Room <4m Height
TOTAL VOLUME THIS ROOM IN CUBIC METERS (m3) | [11 empty] | 120.84 | m3 | Substations Control Room <4m Height
Warehouse <4m Height
Archive Room <4m Height
M (g) |  |  |  | V (m3) |  |  | D (g/m3) | [6 empty] | Boat Engine Compartment <4m Height
Mass of FirePro® Aerosol |  |  |  | Total Volume |  |  | EAD |  |  | SF |  |  |  | Other Large Size Enclosure <4m Height
Extinguishing Application Density (g) |  |  | = | 120.84 | m3 | x | 84 | g/m3 | x | 1.3 | = | 13195.728 | g | Warehouse >4m Height
Substation Control Room >4m Height
RECOMMENDED GENERATOR MODEL(S) SELECTION | [13 empty] | Transformer Room >4m Height
Boat Engine Compartment >4m Height
Recommended Models by Stream Lenth: | [13 empty] | Museum >4m Height
FP-500S, FP-1200, FP-2000, FP-3000 | [13 empty] | Archive Room >4m Height
Recommended Models by Volume: | [13 empty] | Plant Room >4m Height
FP-500S, FP-1200, FP-2000, FP-3000 | [13 empty] | Other Very Large Size Encl. >4m Height
CONFIRM SIZE CORRECTNESS OF GENERATOR RECOMMENDED - ROOM VOLUME Vs GENERATOR COVERAGE
IMPORTANT REMARKS:
1. THIS SOFTWARE IS ONLY A GUIDING TOOL - SELECTION OF GENERATORS IS THE USER's RESPONSIBILITY.
2. ABOVE SELECTION IS JUST A RECOMMENDATION. ENGINEERING JUDGMENT SHOULD BE APPLIED FOR PROPER SELECTION OF GENERATORS TAKING INTO CONSIDERATION ROOM HEIGHT(STREAM LENGTH), GENERATOR ORIENTATION IN RELATION TO THE VOLUME ARRANGEMENT, OPENINGS etc.
3. FOR PROTECTED VOLUMES EXCEEDING 4M HEIGHT GENERATORS SHOULD BE INSTALLED IN STAGGERED
ARRANGEMENT TO ENABLE PROPER TOTAL FLOODING - PLEASE CONSULT MANUFACTURER.
4. ALWAYS CHECK CALCULATIONS FOR CORRECTNESS
| TOTAL VOLUME THIS SECTION | [10 empty] | 120.84 | m3
| TOTAL FirePro® MASS REQUIRED FOR VOLUME 1 | [10 empty] | 13195.728 | g
FirePro Systems Ltd all rights reserved
Note on F8: ENTER UNITS
Note on F10: QUICK CONCENTRATION CALCULATION ENTER VOLUME ONLY IF KNOWN AND ONLY IF IT IS NOT REQUIRED TO BE CALCULATED BELOW
Note on F13: INSERT ROOM NAME/No
Note on F15: ENTER SPACE USAGE/TYPE
Note on F19: Insert Room "LENGTH": For Rectangular Shapes "SIDE 1" : For Triangular Shapes or "RADIUS": For Semi-Cylindrical & Cylindrical Shapes LEAVE BLANC IF VOLUME HAS BEEN INSERTED DIRECTLY IN THE "VOLUME" BOX ABOVE
Note on I19: Insert Room "WIDTH": For Rectangular Shapes "SIDE 2" : For Triangular Shapes or LEAVE BLANC: For Semi-Cylindrical & Cylindrical Shapes LEAVE BLANC IF VOLUME HAS BEEN INSERTED DIRECTLY IN THE "VOLUME" BOX ABOVE
Note on L19: Insert Room "HEIGHT": For ALL Shapes LEAVE BLANC IF VOLUME HAS BEEN INSERTED DIRECTLY IN THE "VOLUME" BOX ABOVE
Note on R19: Calculated Automatically
Note on F24: Enter Stream Required to Reach Fire Effectively - According to Generator's Location/Orientation, Obstacles and Likely Source of Fire Location
Note on F26: ENTER ADDITIONAL SAFETY FACTOR IF REQUIRED ACCORDING TO ROOM INFILTRATION, OPENINGS ETC. CONSIDERABLE ATTENTION SHOULD BE ADHERED TO SO THAT ALL POSSIBLE OPENINGS, VENTILATION AND AIR CIRCULATION MEANS ARE SHUT OFF PRIOR TO GENERATORS ACTIVATION
Note on R30: CELL IS CALCULATED AUTOMATICALLY
Note on R35: CELL IS CALCULATED AUTOMATICALLY

## Volume 1 Generator Selection
Installer company
FirePro®
G e n e r a t o r S e l e c t i o n S h e e t
VOLUME 1
Mass of FirePro® Aerosol
Extinguishing Material Required (g) | [6 empty] | 13195.728 | g
VOLUME 1 | [6 empty] | 120.84 | m3
RECOMMENDED GENERATOR MODEL(S) SELECTION
BY Stream Length |  |  |  |  | By Volume Capacity
FP-500S, FP-1200, FP-2000, FP-3000 |  |  |  |  | FP-500S, FP-1200, FP-2000, FP-3000
MODEL SELECTION
REF | MODEL |  |  | Concentr. |  | QTY |  |  | TOTAL CONCENTRATION |  |  |  | Cost
|  |  |  | (g) |  |  |  |  | (g) |  |  |  | Analysis
1 | FP-8 |  | 0 | 8 | [6 empty] | 0 |  | 11.8 | 0
2 | FP-20E |  | 0 | 20 | [6 empty] | 0 |  | 22.5 | 0
3 | FP-20S |  | 0 | 20 | [6 empty] | 0 |  | 19.5 | 0
4 | FP-40S |  | 0 | 40 | [6 empty] | 0 |  | 45 | 0
5 | FP-80 |  | 0 | 80 | [6 empty] | 0 |  | 66 | 0
6 | FP-80S |  | 0 | 80 | [6 empty] | 0 |  | 66 | 0
7 | FP-100S |  | 0 | 100 | [6 empty] | 0 |  | 98 | 0
8 | FP-200S |  | 0 | 200 | [6 empty] | 0 |  | 113 | 0
9 | FP-500S |  | 0 | 500 | [6 empty] | 0 |  | 168 | 0
10 | FP-1200 |  | 1200 | 1200 |  | 1 |  |  |  |  | 1200 |  | 280 | 280
11 | FP-2000 |  | 0 | 2000 | [6 empty] | 0 |  | 325 | 0
12 | FP-3000 |  | 12000 | 3000 |  | 4 |  |  |  |  | 12000 |  | 385 | 1540
13 | FP-5700 |  | 0 | 5700 | [6 empty] | 0 |  | 660 | 0
14 | Heat Impulse Translator (H.I.T.) |  | #VALUE! | (meters) | [8 empty] | 0 | 0 | Thermocord
[7 empty] | TOTAL |  |  |  | 13200 | g |  | 1820 | Total FirePro Cost
Volume 1
| (+) EXCESS / (-) SHORTAGE CONCENTRATION | [8 empty] | 4.272 |  | g
| DEVIATION (+/-) |  |  | 0.03237%
CHECKED FOR CORRECTNESS:
APPROVED - CONCENTRATION IS WITHIN +5%
REMARKS:
AEROSOL TOTAL FLOODING COVERAGE IN PROTECTED SPACE SHALL BE ACHIEVED WITH EVEN DISTRIBUTION OF GENERATORS AS PER MANUFACTURER'S RECOMMENDATIONS
FirePro Systems Ltd all rights reserved
DO NOT USE FP5700 - HEIGHT IS TO SMALL
Note on L10: CELL IS CALCULATED AUTOMATICALLY
Note on L12: CELL IS CALCULATED AUTOMATICALLY
Note on I34: SELECT THIS MODEL ONLY IF ROOM HEIGHT EXCEEDS 4M
Note on K35: Insert Length of Thermocord Required for this volume

## Generator Cost Estimate
Installer company
FirePro®
C o s t E s t i m a t i o n S h e e t
Fire Extinguishing Aerosol Generators
MODEL SELECTION
REF | MODEL |  | Concentr. | QTY |  | Unit Price |  | Amount
|  |  | (g) |  |  | (Euro)
1 | FP-8 |  | 8 | 0
2 | FP-20E |  | 20 | 0
3 | FP-20S |  | 20 | 0
4 | FP-40S |  | 40 | 0
5 | FP-80 |  | 80 | 0
6 | FP-80S |  | 80 | 0
7 | FP-100S |  | 100 | 0
8 | FP-200S |  | 200 | 0
9 | FP-500S |  | 500 | 0
10 | FP-1200 |  | 1200 | 0
11 | FP-2000 |  | 2000 | 0
12 | FP-3000 |  | 3000 | 0
13 | FP-5700 |  | 5700 | 0
14 | Heat Impulse Translator (H.I.T.) |  |  | 0
Manufactured by CELANOVA LTD/FirePro Systems Ltd | [6 empty] | TOTAL | 0
[7 empty] | Electrical Accessories | 0
Installation Cost
Transport
Other
[7 empty] | Subtotal | 0
Discount
[7 empty] | Subtotal | 0
[5 empty] | VAT @ |  | 18% | 0
[7 empty] | TOTAL | 0
FirePro Systems Ltd all rights reserved
DO NOT USE FP5700 - HEIGHT IS TO SMALL
Note on N19: Insert Your Currency
Note on N20: Insert Your Selling Price for the Unit
Note on N21: Insert Your Selling Price for the Unit
Note on N22: Insert Your Selling Price for the Unit
Note on N23: Insert Your Selling Price for the Unit
Note on N24: Insert Your Selling Price for the Unit
Note on N25: Insert Your Selling Price for the Unit
Note on N26: Insert Your Selling Price for the Unit
Note on N27: Insert Your Selling Price for the Unit
Note on N28: Insert Your Selling Price for the Unit
Note on N29: Insert Your Selling Price for the Unit
Note on I30: SELECT THIS MODEL ONLY IF ROOM HEIGHT EXCEEDS 4M
Note on N30: Insert Your Selling Price for the Unit
Note on N31: Insert Your Selling Price for the Unit
Note on N32: Insert Your Selling Price for the Unit
Note on N33: Insert Your Selling Price for the Unit

## Electrical Cost Estimate
Installer company
FirePro®
C o s t E s t i m a t i o n S h e e t
Electrical Equipment Selection
Electrical Components & Accessories
REF | MODEL | Product | QTY | Unit Price |  | Amount
|  | Code |  | (Euro)
1 | FirePro - Kentec XT Ext. Panel | FP-K 11031M2 | 0 | 0
2 | FirePro Sequential Activators | FP-SA/GEN2.0 | 0 | 0
3 | Optical Smoke Detector c/w Base | S100 | 0 | 0
4 | Heat Detector - Fixed Temp. (78oC) | S300 | 0 | 0
5 | Rate-of-Rise Heat Detectors (58oC) | S400 | 0 | 0
6 | Universal Resistor Detector Base | UBR100 | 0 | 0
7 | Sounder & Beacon 24V dc | FS 24 | 0 | 0
8 | External Sounder & Beacon | Flashni | 0 | 0
9 | Abort Switch | ES100 | 0 | 0
10 | GAS Sign | FL 24 | 0 | 0
11 | GAS Sign Waterproof | FL 65 | 0 | 0
12 | Bell 24V | MBM 246 | 0 | 0
13 | Electronic Sounder 9-30V | MWS 423 | 0 | 0
14 | Cable Fire Rated Twisted Shielded | 2-core - 1.0mm2 | 0 | 0
15 | Cable Fire Rated Twisted Shielded | 2-core - 1.5mm2 | 0 | 0
16 |  |  | 0 | 0
[5 empty] | TOTAL | 0
Electrical Accessories
Installation Cost
Transport
Other
[5 empty] | Subtotal | 0
Discount
[5 empty] | Subtotal | 0
[5 empty] | TOTAL - ELECTRICAL ACCESSORIES | 0
FirePro Systems Ltd all rights reserved
Note on N19: Insert Your Currency
Note on N20: Insert Your Selling Price for the Unit
Note on N21: Insert Your Selling Price for the Unit
Note on N22: Insert Your Selling Price for the Unit
Note on N23: Insert Your Selling Price for the Unit
Note on N24: Insert Your Selling Price for the Unit
Note on N25: Insert Your Selling Price for the Unit
Note on N26: Insert Your Selling Price for the Unit
Note on N27: Insert Your Selling Price for the Unit
Note on N28: Insert Your Selling Price for the Unit
Note on N29: Insert Your Selling Price for the Unit
Note on N30: Insert Your Selling Price for the Unit
Note on N31: Insert Your Selling Price for the Unit
Note on N32: Insert Your Selling Price for the Unit
Note on N33: Insert Your Selling Price for the Unit
Note on N34: Insert Your Selling Price for the Unit
Note on N35: Insert Your Selling Price for the Unit

## Important Information
FirePro®
I m p o r t a n t D e s i g n I n f o r m a t I o n S h e e t
Design Considerations
(FirePro User Manual Extract)
Different factors are important for the calculation of the amount of FirePro® aerosol required, and they are:
a) The fire class
b) Total volume of the room
c) Ventilation in the room
d) Atmospheric pressure present
e) Protection time in the room
f) The added safety factor
g) The siting of the given type of unit
Some of the above factors are fixed factors, others have limited variability. The fixed calculation factors are:
- volume of the room to be protected
- the fire class of the substances present in the room
The basic method of calculation is the formula: |  |  | M = V x D
M = total flooding quantity, in gr
V = protected volume (enclosure), in m3
D = Design Application Density, in gr/m3 (see table 7.0.1)
as per test protocols: UL2127, CEN/TR 15276 1/2, KIWA BRL-K23001/3, ISO DIS 15779
[(D = Extinguishing Application Density EAD x Safety Factor SF(1.3)]
as per International Standards: NFPA 2010, CEN/TR 15276 1/2, ISO DIS 15779
FirePro Systems Ltd all rights reserved

## Design Factors Data Sheet
DO NOT ALTER THESE CONCENTRATIONS
Class A - Combustible Solids / Electically Energized Fires | [6 empty] | 76.4
Class B - Combustible Liquids | [6 empty] | 55.4
Class C - Combustible Gases | [6 empty] | 49.8
Class F - Flammable Oil & Fats | [6 empty] | 80.82
|  |  | GENERATORS STREAM GROUPING | [5 empty] | VOLUME RANGE GROUPING
|  |  | S.L. |  |  |  | STREAM RANGE (m) |  | VOLUME RANGE (m3)
FP-8 | Up to 0.5 |  | UP TO 0.6 | FP-8, FP-20E, FP20S, FP40S, FP80S |  |  | 0.1 | 0.6 | 0.0001 | 0.8 | FP-8, FP-20E, FP20S, FP40S, FP80S
FP-20E | Up to 0.6 | Both Sides
FP-20S | Up to 0.6 | Both Sides
FP-40S | Up to 2.4 | Both Sides
FP-80S | Up to 4.0 | Both Sides
FP-100S | Up to 1.0 |  | 0.6<SL<2.5 | FP-80S, FP-100S, FP-200S, FP-500S |  |  | 0.6 | 2.5 | 0.8 | 10 | FP-80S, FP-100S, FP-200S, FP-500S
FP-200S | Up to 2.0
FP-500S | Up to 2.5
FP-1200 | Up to 3.5
FP-2000 | Up to 3.5 |  | 2.5<SL<4.0 | FP-500S, FP-1200, FP-2000, FP-3000 |  |  | 2.5 | 4 | 10 | 500 | FP-500S, FP-1200, FP-2000, FP-3000
FP-3000 | Up to 4.0
FP-5700 | 4.0<SL<8.0 |  | 4.0<SL<8.0 | FP-5700 |  |  | 4 | 8 | 500 | 3000 | FP-5700
FirePro®
Fire Extinguishing Aerosol Generators
Aerosol Temperature and Operation time
|  | Discharge Outlets | Discharge Stream Length (m) | Discharge temperature (oC) |  |  | Discharge duration (sec)
Ref. | Model |  |  | L1,(m) | L1-L2,(m) | L2-L3,(m) | Min. | Max.
1 | FP-8 | 1 | 0.5 | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 3 | 6
2 | FP-20E | 2 | 0.3 | 0 | 0-0.1 | 0.1-0.2 | 3 | 6
3 | FP-20S | 2 | 0.3 | 0 | 0-0.1 | 0.1-0.2 | 3 | 6
4 | FP-40S | 2 | 1.2 | 0 | 0-0.1 | 0-0.3 | 5 | 10
5 | FP-80S | 2 | 2 | 0 | 0-0.1 | 0.1-0.3 | 4 | 8
6 | FP-100S | 1 | 1 | 0 | 0-0.2 | 0.2-0.4 | 5 | 10
7 | FP-100S w/n | 1 | 1 | 0 | 0-0.1 | 0.1-0.2 | 5 | 10
8 | FP-200S | 1 | 2 | 0 | 0-0.3 | 0.3-1.4 | 5 | 10
9 | FP-200S w/n | 1 | 1.5 | 0 | 0-0.1 | 0.1-0.3 | 5 | 10
10 | FP-500S | 1 | 2.5 | 0 | 0-0.5 | 0.5-1.8 | 5 | 10
11 | FP-500S w/n | 1 | 2 | 0 | 0-0.1 | 0.1-0.5 | 5 | 10
12 | FP-1200 | 1 | 3.5 | 0 | 0 | 0-1.0 | 10 | 15
13 | FP-2000 | 1 | 3.5 | 0 | 0 | 0-1.0 | 10 | 15
14 | FP-3000 | 1 | 4 | 0 | 0-0.5 | 0.5-1.5 | 15 | 20
15 | FP-5700 | 1 | 8 | 0 | 0-0.5 | 0.5-1.5 | 15 | 20
L1 = Distance in meters between the outlet and the point where the Temperature is > 300oC
L2 = Distance in meters between the outlet and the point where the Temperature is < 200oC
L3 = Distance in meters between the outlet and the point where the Temperature is < 75oC
TH= | Thermocord
M= | Manual
E= | Electrical
w/n | With nozzle
FirePro®
Fire Extinguishing Aerosol Generators
Technical Information Table
|  | Discharge | Discharge | Discharge temperature (oC) |  |  | Discharge duration (sec)
Ref. | Model | outlets | length (m) | L1,(m) | L1-L2,(m) | L2-L3,(m) | Min. | Max.
1 | FP-8 | 1 | 0.5 | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 3 | 6
2 | FP-20E | 2 | 0.3 | 0 | 0-0.1 | 0.1-0.2 | 3 | 6
3 | FP-20S | 2 | 0.3 | 0 | 0-0.1 | 0.1-0.2 | 3 | 6
4 | FP-40S | 2 | 1.2 | 0 | 0-0.1 | 0-0.3 | 5 | 10
5 | FP-80S | 2 | 2 | 0 | 0-0.1 | 0.1-0.3 | 4 | 8
6 | FP-100S | 1 | 1 | 0 | 0-0.2 | 0.2-0.4 | 5 | 10
7 | FP-100S w/n | 1 | 1 | 0 | 0-0.1 | 0.1-0.2 | 5 | 10
8 | FP-200S | 1 | 2 | 0 | 0-0.3 | 0.3-1.4 | 5 | 10
9 | FP-200S w/n | 1 | 1.5 | 0 | 0-0.1 | 0.1-0.3 | 5 | 10
10 | FP-500S | 1 | 2.5 | 0 | 0-0.5 | 0.5-1.8 | 5 | 10
11 | FP-500S w/n | 1 | 2 | 0 | 0-0.1 | 0.1-0.5 | 5 | 10
12 | FP-1200 | 1 | 3.5 | 0 | 0 | 0-1.0 | 10 | 15
13 | FP-2000 | 1 | 3.5 | 0 | 0 | 0-1.0 | 10 | 15
14 | FP-3000 | 1 | 4 | 0 | 0-0.5 | 0.5-1.5 | 15 | 20
15 | FP-5700 | 1 | 8 | 0 | 0-0.5 | 0.5-1.5 | 15 | 20
Activation mode:
TH= | Thermocord
M= | Manual
E= | Electrical
w/n = | With Nozzle
Self-activation temperature of extinguishing material 300 °C
Note on J2: DO NOT CHANGE THESE CONCENTRATION FACTORS
Note on J3: DO NOT CHANGE THESE CONCENTRATION FACTORS
Note on J4: DO NOT CHANGE THESE CONCENTRATION FACTORS
Note on J5: DO NOT CHANGE THESE CONCENTRATION FACTORS

## Design Guidelines
SCROLL DOWN TO READ