## HT LT -04
VENTILATION CALCULATION OF THE H.T & L.T ROOMS
1- | ASSUMPTIONS
| Ambient temp. = |  |  | 115 F
| Acceptable Air Change/Hr = |  |  | 10 | times
2- | CALCULATION
2.1 | Ventilated Air Quantity for H.T Room |  |  |  | (Room Ref. S/S-4)
| Room Volume = |  | 331.7 | Cu.M
|  | = | 11704.881 | Cu.Ft
Where :-
| Length L = |  | 10.7 | M
| Width D = |  | 6.2 | M
| Hight H = |  | 5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 117048.81 | Cu.Ft/Hr
|  |  |  | = | 1950.8135 | CFM
| ** Adopt |  | Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 2000 | CFM | AND | 1 KW
2.2 | Ventilated Air Quantity for L.T Room |  |  |  | (Room Ref. S/S-4)
| Room Volume = |  | 278.2 | Cu.M
|  | = | 9816.997 | Cu.Ft
Where :-
| Length L = |  | 10.7 | M
| Width D = |  | 5.2 | M
| Hight H = |  | 5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 98169.9697 | Cu.Ft/Hr
|  |  |  | = | 1636.1662 | CFM
| ** Adopt |  | Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 1600 | CFM | AND | 1 KW

## HT LT-1,5,6
VENTILATION CALCULATION OF THE H.T & L.T ROOMS
1- | ASSUMPTIONS
| Ambient temp. = |  |  | 115 F
| Acceptable Air Change/Hr = |  |  | 10 | times
2- | CALCULATION
2.1 | Ventilated Air Quantity for H.T Room |  |  |  | (Room Ref. S/S-1,5,6)
| Room Volume = |  | 248 | Cu.M
|  | = | 8751.3129 | Cu.Ft
Where :-
| Length L = |  | 8 | M
| Width D = |  | 6.2 | M
| Hight H = |  | 5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 87513.129 | Cu.Ft/Hr
|  |  |  | = | 1458.5521 | CFM
| ** Adopt |  | Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 1600 | CFM | AND | 1 KW
2.2 | Ventilated Air Quantity for L.T Room |  |  |  | (Room Ref. S/S-1,5,6)
| Room Volume = |  | 208 | Cu.M
|  | = | 7339.8108 | Cu.Ft
Where :-
| Length L = |  | 8 | M
| Width D = |  | 5.2 | M
| Hight H = |  | 5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 73398.1082 | Cu.Ft/Hr
|  |  |  | = | 1223.3018 | CFM
| ** Adopt |  | Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 1200 | CFM | AND | 1 KW

## HT LT-2,3
VENTILATION CALCULATION OF THE H.T & L.T ROOMS
1 | ASSUMPTIONS
| Ambient temp. = |  |  | 115 F
| Acceptable Air Change/Hr = |  |  | 10 | times
2 | CALCULATION
2.1 | Ventilated Air Quantity for H.T Room |  |  |  | (Room Ref. S/S-2,3)
| Room Volume = |  | 126 | Cu.M
|  | = | 4446.2316 | Cu.Ft
Where :-
| Length L = |  | 6 | M
| Width D = |  | 6 | M
| Hight H = |  | 3.5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 44462.3155 | Cu.Ft/Hr
|  |  |  | = | 741.0386 | CFM
** Adopt one Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 741.0386 | CFM | AND | 1 KW
2.2 | Ventilated Air Quantity for L.T Room |  |  |  | (Room Ref. S/S-2,3)
| Room Volume = |  | 300 | Cu.M
|  | = | 10586.2656 | Cu.Ft
Where :-
| Length L = |  | 8 | M
| Width D = |  | 7.5 | M
| Hight H = |  | 5 | M
| Acceptable Air Change/Hr = |  |  | 10 | Times
THEN :-
| Ventilated Air Quantity for H.T Room = |  |  |  | 105862.656 | Cu.Ft/Hr
|  |  |  | = | 1764.3776 | CFM
** Adopt one Fan wall mounted axial type with Ext. Est. Static Pressure of 0.5 " W.G
| Fan Capacity = |  | 1764.3776 | CFM | AND | 1 KW