## sub-st. no. 1
VENTILATION CALCULATION FOR THE TRANSFORMER ROOM
1 | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 1
| - Number Of Transformers | [6 empty] | 1 | Nos.
| - Transformer Rateing | [5 empty] | = | 1600 | KVA
| - Number Of Transformers | [5 empty] | = | 1 | Nos.
| - Transformer Rateing | [5 empty] | = | 1250 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2 | CALCULATION
Heat Loss / Transformer
| = ( | 1 | x | 1600 | + | 1 | x | 1250 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 45.6 |  | KW
| = | 45600 |  | Watt
Total Heat Dissipation
=
| = | 45600 |  |  | x | 3.413
| = | 155632.8 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 13343.0041 |  | CFM
3 | VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 2
| Fan Capacity / Each |  |  |  | = | 6671.5021 | = |  |  | CFM
| Fan rating KW/Each |  |  |  | = | 1.3689 |  | KW
| Fan st. Pressure |  |  |  | = | 1 |  | IN.WG

## sub-st.no 2
VEVTILATION CALCULATION FOR THE TRANSFORMER ROOM
1- | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 2
| - Number Of Transformers | [5 empty] | = | 0 | Nos.
| - Transformer Rateing | [5 empty] | = | 0 | KVA
| - Number Of Transformers | [5 empty] | = | 3 | Nos.
| - Transformer Rateing | [5 empty] | = | 1250 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2- | CALCULATION
Heat Loss / Transformer
| = ( | 0 | x | 0 | + | 3 | x | 1250 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 60 |  | KW
| = | 60000 |  | Watt
Total Heat Dissipation
=
| = | 60000 |  |  | x | 3.413
| = | 204780 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 17556.5844 |  | CFM
VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 2
| Fan Capacity / Each |  |  |  | = | 8778.2922 | = |  |  | CFM
| Fan rating KW/Each |  |  |  | = | 1.0716 |  | KW
| Fan st. Pressure |  |  |  | = | 0.5 |  | IN.WG

## sub-st. no.3
VEVTILATION CALCULATION FOR THE TRANSFORMER ROOM
PROJECT :
1- | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 1
| - Number Of Transformers | [5 empty] | = | 1 | Nos.
| - Transformer Rateing | [5 empty] | = | 1000 | KVA
| - Number Of Transformers | [5 empty] | = | 0 | Nos.
| - Transformer Rateing | [5 empty] | = | 1000 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2- | CALCULATION
Heat Loss / Transformer
| = ( | 1 | x | 1000 | + | 0 | x | 1000 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 16 |  | KW
| = | 16000 |  | Watt
Total Heat Dissipation
=
| = | 16000 |  |  | x | 3.413
| = | 54608 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 4681.7558 |  | CFM
VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 1
| Fan Capacity / Each |  |  |  | = | 4681.7558 | = |  |  | CFM
| Fan rating KW/Each |  |  |  | = | 1.1097 |  | KW
| Fan st. Pressure |  |  |  | = | 1 |  | IN.WG

## no. 4
VENTILATION CALCULATION FOR THE TRANSFORMER ROOM
1- | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 4
| - Number Of Transformers | [5 empty] | = | 6 | Nos.
| - Transformer Rateing | [5 empty] | = | 1600 | KVA
| - Number Of Transformers | [5 empty] | = | 4 | Nos.
| - Transformer Rateing | [5 empty] | = | 0 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2- | CALCULATION
Heat Loss / Transformer
| = ( | 6 | x | 1600 | + | 4 | x | 0 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 153.6 |  | KW
| = | 153600 |  | Watt
Total Heat Dissipation
=
| = | 153600 |  |  | x | 3.413
| = | 524236.8 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 44944.856 |  | CFM
VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 3
| Fan Capacity / Each |  |  |  | = | 14981.6187 | = |  |  | CFM
| Fan rating KW/Each |  |  |  | = | 2.4511 |  | KW
| Fan st. Pressure |  |  |  | = | 1 |  | IN.WG

## no. 5
VEVTILATION CALCULATION FOR THE TRANSFORMER ROOM
1- | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 5
| - Number Of Transformers | [5 empty] | = | 2 | Nos.
| - Transformer Rateing | [5 empty] | = | 1600 | KVA
| - Number Of Transformers | [5 empty] | = | 0 | Nos.
| - Transformer Rateing | [5 empty] | = | 0 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2- | CALCULATION
Heat Loss / Transformer
| = ( | 2 | x | 1600 | + | 0 | x | 0 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 51.2 |  | KW
| = | 51200 |  | Watt
Total Heat Dissipation
=
| = | 51200 |  |  | x | 3.413
| = | 174745.6 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 14981.6187 |  | CFM
VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 2
| Fan Capacity / Each |  |  |  | = | 7490.8093 | = | 6000 |  | CFM
| Fan rating KW/Each |  |  |  | = | 0.98779 |  | KW
| Fan st. Pressure |  |  |  | = | 0.5 |  | IN.WG

## no. 6
VEVTILATION CALCULATION FOR THE TRANSFORMER ROOM
1- | ASSUMPTION
| - Ambient Temperature | [5 empty] | = | 115 | F
| - Max. Allowed Temp. Rise | [5 empty] | = | 10.8 | F
| - Sub- Station Ref. No. | [6 empty] | 6
| - Number Of Transformers | [5 empty] | = | 2 | Nos.
| - Transformer Rateing | [5 empty] | = | 1250 | KVA
| - Number Of Transformers | [5 empty] | = | 0 | Nos.
| - Transformer Rateing | [5 empty] | = | 0 | KVA
| - Power Factor | [5 empty] | = | 0.8
| - Transformer Eff. | [5 empty] | = | 0.98
2- | CALCULATION
Heat Loss / Transformer
| = ( | 2 | x | 1250 | + | 0 | x | 0 | )x | 0.8 | x | ( 1 - | 0.98 | )
| = | 40 |  | KW
| = | 40000 |  | Watt
Total Heat Dissipation
=
| = | 40000 |  |  | x | 3.413
| = | 136520 |  |  |  | Btu/hr
| = | 1.08 | x | CFM | x | Temp. Rise
| = | 1.08 | x | CFM | x | 10.8
Air Quantity Required for ventilation
Then :-
| The Air Quantity |  |  |  | = | 11704.3896 |  | CFM
VENTILATION SYSTEM DISCRIPTION
| Number of fans |  |  |  | = | 2
| Fan Capacity / Each |  |  |  | = | 5852.1948 | = | 6000 |  | CFM
| Fan rating KW/Each |  |  |  | = | 0.88108 |  | KW
| Fan st. Pressure |  |  |  | = | 0.5 |  | IN.WG
FAN (HP) = St. Pr.(INCH) X Flow (CFM) /( 0.9 X6356)