## Chart Data
Elevation | 0
atm | 29.921 | RH
|  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
DB Inc | Dry Bulb
1 | 32 | 2.6401 | 5.2802 | 7.9203 | 10.5605 | 13.2006 | 15.8407 | 18.4808 | 21.1209 | 23.761 | 26.4011
| 33 | 2.7496 | 5.4992 | 8.2488 | 10.9984 | 13.748 | 16.4976 | 19.2472 | 21.9968 | 24.7464 | 27.496
| 34 | 2.8628 | 5.7256 | 8.5885 | 11.4513 | 14.3141 | 17.1769 | 20.0397 | 22.9025 | 25.7654 | 28.6282
| 35 | 2.9802 | 5.9604 | 8.9405 | 11.9207 | 14.9009 | 17.8811 | 20.8613 | 23.8414 | 26.8216 | 29.8018
| 36 | 3.1018 | 6.2036 | 9.3055 | 12.4073 | 15.5091 | 18.6109 | 21.7127 | 24.8146 | 27.9164 | 31.0182
| 37 | 3.2279 | 6.4557 | 9.6836 | 12.9115 | 16.1394 | 19.3672 | 22.5951 | 25.823 | 29.0509 | 32.2787
| 38 | 3.3585 | 6.717 | 10.0755 | 13.4339 | 16.7924 | 20.1509 | 23.5094 | 26.8679 | 30.2264 | 33.5849
| 39 | 3.4938 | 6.9876 | 10.4814 | 13.9752 | 17.469 | 20.9628 | 24.4566 | 27.9504 | 31.4442 | 34.938
| 40 | 3.634 | 7.2679 | 10.9019 | 14.5358 | 18.1698 | 21.8037 | 25.4377 | 29.0717 | 32.7056 | 36.3396
| 41 | 3.7791 | 7.5582 | 11.3374 | 15.1165 | 18.8956 | 22.6747 | 26.4538 | 30.2329 | 34.0121 | 37.7912
| 42 | 3.9294 | 7.8589 | 11.7883 | 15.7177 | 19.6472 | 23.5766 | 27.5061 | 31.4355 | 35.3649 | 39.2944
| 43 | 4.0851 | 8.1702 | 12.2552 | 16.3403 | 20.4254 | 24.5105 | 28.5955 | 32.6806 | 36.7657 | 40.8508
| 44 | 4.2462 | 8.4924 | 12.7386 | 16.9848 | 21.231 | 25.4772 | 29.7234 | 33.9696 | 38.2158 | 42.462
| 45 | 4.413 | 8.826 | 13.2389 | 17.6519 | 22.0649 | 26.4779 | 30.8908 | 35.3038 | 39.7168 | 44.1298
| 46 | 4.5856 | 9.1712 | 13.7568 | 18.3423 | 22.9279 | 27.5135 | 32.0991 | 36.6847 | 41.2703 | 45.8558
| 47 | 4.7642 | 9.5284 | 14.2926 | 19.0568 | 23.821 | 28.5852 | 33.3494 | 38.1136 | 42.8778 | 47.642
| 48 | 4.949 | 9.898 | 14.847 | 19.7961 | 24.7451 | 29.6941 | 34.6431 | 39.5921 | 44.5411 | 49.4901
| 49 | 5.1402 | 10.2804 | 15.4206 | 20.5608 | 25.701 | 30.8412 | 35.9815 | 41.1217 | 46.2619 | 51.4021
| 50 | 5.338 | 10.676 | 16.0139 | 21.3519 | 26.6899 | 32.0279 | 37.3659 | 42.7039 | 48.0418 | 53.3798
| 51 | 5.5425 | 11.0851 | 16.6276 | 22.1701 | 27.7127 | 33.2552 | 38.7977 | 44.3403 | 49.8828 | 55.4253
| 52 | 5.7541 | 11.5081 | 17.2622 | 23.0163 | 28.7704 | 34.5244 | 40.2785 | 46.0326 | 51.7866 | 57.5407
| 53 | 5.9728 | 11.9456 | 17.9184 | 23.8912 | 29.864 | 35.8368 | 41.8096 | 47.7824 | 53.7552 | 59.7281
| 54 | 6.199 | 12.3979 | 18.5969 | 24.7958 | 30.9948 | 37.1937 | 43.3927 | 49.5916 | 55.7906 | 61.9895
| 55 | 6.4327 | 12.8655 | 19.2982 | 25.7309 | 32.1637 | 38.5964 | 45.0291 | 51.4619 | 57.8946 | 64.3274
| 56 | 6.6744 | 13.3488 | 20.0232 | 26.6975 | 33.3719 | 40.0463 | 46.7207 | 53.3951 | 60.0695 | 66.7438
| 57 | 6.9241 | 13.8483 | 20.7724 | 27.6965 | 34.6207 | 41.5448 | 48.4689 | 55.3931 | 62.3172 | 69.2413
| 58 | 7.1822 | 14.3645 | 21.5467 | 28.7289 | 35.9111 | 43.0934 | 50.2756 | 57.4578 | 64.6401 | 71.8223
| 59 | 7.4489 | 14.8978 | 22.3467 | 29.7957 | 37.2446 | 44.6935 | 52.1424 | 59.5913 | 67.0402 | 74.4891
| 60 | 7.7244 | 15.4489 | 23.1733 | 30.8978 | 38.6222 | 46.3467 | 54.0711 | 61.7956 | 69.52 | 77.2445
| 61 | 8.0091 | 16.0182 | 24.0273 | 32.0364 | 40.0455 | 48.0546 | 56.0636 | 64.0727 | 72.0818 | 80.0909
| 62 | 8.3031 | 16.6062 | 24.9094 | 33.2125 | 41.5156 | 49.8187 | 58.1218 | 66.4249 | 74.7281 | 83.0312
| 63 | 8.6068 | 17.2136 | 25.8204 | 34.4272 | 43.034 | 51.6408 | 60.2476 | 68.8544 | 77.4612 | 86.068
| 64 | 8.9204 | 17.8409 | 26.7613 | 35.6817 | 44.6021 | 53.5226 | 62.443 | 71.3634 | 80.2839 | 89.2043
| 65 | 9.2443 | 18.4886 | 27.7329 | 36.9772 | 46.2215 | 55.4658 | 64.71 | 73.9543 | 83.1986 | 92.4429
| 66 | 9.5787 | 19.1574 | 28.7361 | 38.3148 | 47.8935 | 57.4722 | 67.0509 | 76.6295 | 86.2082 | 95.7869
| 67 | 9.9239 | 19.8479 | 29.7718 | 39.6958 | 49.6197 | 59.5437 | 69.4676 | 79.3915 | 89.3155 | 99.2394
| 68 | 10.2804 | 20.5607 | 30.8411 | 41.1214 | 51.4018 | 61.6822 | 71.9625 | 82.2429 | 92.5232 | 102.8036
| 69 | 10.6483 | 21.2965 | 31.9448 | 42.5931 | 53.2414 | 63.8896 | 74.5379 | 85.1862 | 95.8344 | 106.4827
| 70 | 11.028 | 22.056 | 33.084 | 44.1121 | 55.1401 | 66.1681 | 77.1961 | 88.2241 | 99.2521 | 110.2801
| 71 | 11.4199 | 22.8399 | 34.2598 | 45.6797 | 57.0997 | 68.5196 | 79.9395 | 91.3595 | 102.7794 | 114.1993
| 72 | 11.8244 | 23.6488 | 35.4732 | 47.2975 | 59.1219 | 70.9463 | 82.7707 | 94.5951 | 106.4195 | 118.2439
| 73 | 12.2417 | 24.4835 | 36.7252 | 48.967 | 61.2087 | 73.4504 | 85.6922 | 97.9339 | 110.1756 | 122.4174
| 74 | 12.6724 | 25.3447 | 38.0171 | 50.6895 | 63.3619 | 76.0342 | 88.7066 | 101.379 | 114.0513 | 126.7237
| 75 | 13.1167 | 26.2333 | 39.35 | 52.4667 | 65.5833 | 78.7 | 91.8167 | 104.9333 | 118.05 | 131.1667
| 76 | 13.575 | 27.1501 | 40.7251 | 54.3001 | 67.8751 | 81.4502 | 95.0252 | 108.6002 | 122.1753 | 135.7503
| 77 | 14.0479 | 28.0957 | 42.1436 | 56.1915 | 70.2393 | 84.2872 | 98.3351 | 112.3829 | 126.4308 | 140.4787
| 78 | 14.5356 | 29.0712 | 43.6068 | 58.1424 | 72.678 | 87.2136 | 101.7492 | 116.2848 | 130.8204 | 145.356
| 79 | 15.0387 | 30.0773 | 45.116 | 60.1547 | 75.1934 | 90.232 | 105.2707 | 120.3094 | 135.348 | 150.3867
| 80 | 15.5575 | 31.115 | 46.6726 | 62.2301 | 77.7876 | 93.3451 | 108.9027 | 124.4602 | 140.0177 | 155.5752
| 81 | 16.0926 | 32.1852 | 48.2779 | 64.3705 | 80.4631 | 96.5557 | 112.6483 | 128.741 | 144.8336 | 160.9262
| 82 | 16.6444 | 33.2889 | 49.9333 | 66.5777 | 83.2222 | 99.8666 | 116.5111 | 133.1555 | 149.7999 | 166.4444
| 83 | 17.2135 | 34.4269 | 51.6404 | 68.8538 | 86.0673 | 103.2808 | 120.4942 | 137.7077 | 154.9212 | 172.1346
| 84 | 17.8002 | 35.6004 | 53.4006 | 71.2008 | 89.001 | 106.8012 | 124.6014 | 142.4016 | 160.2018 | 178.002
| 85 | 18.4052 | 36.8103 | 55.2155 | 73.6207 | 92.0259 | 110.431 | 128.8362 | 147.2414 | 165.6466 | 184.0517
| 86 | 19.0289 | 38.0578 | 57.0868 | 76.1157 | 95.1446 | 114.1735 | 133.2024 | 152.2314 | 171.2603 | 190.2892
| 87 | 19.672 | 39.344 | 59.016 | 78.6879 | 98.3599 | 118.0319 | 137.7039 | 157.3759 | 177.0479 | 196.7199
| 88 | 20.3349 | 40.6699 | 61.0048 | 81.3398 | 101.6747 | 122.0097 | 142.3446 | 162.6796 | 183.0145 | 203.3495
| 89 | 21.0184 | 42.0368 | 63.0552 | 84.0736 | 105.0919 | 126.1103 | 147.1287 | 168.1471 | 189.1655 | 210.1839
| 90 | 21.7229 | 43.4458 | 65.1688 | 86.8917 | 108.6146 | 130.3375 | 152.0604 | 173.7833 | 195.5063 | 217.2292
| 91 | 22.4492 | 44.8983 | 67.3475 | 89.7966 | 112.2458 | 134.695 | 157.1441 | 179.5933 | 202.0424 | 224.4916
| 92 | 23.1978 | 46.3955 | 69.5933 | 92.791 | 115.9888 | 139.1866 | 162.3843 | 185.5821 | 208.7798 | 231.9776
| 93 | 23.9694 | 47.9388 | 71.9082 | 95.8775 | 119.8469 | 143.8163 | 167.7857 | 191.7551 | 215.7245 | 239.6939
| 94 | 24.7647 | 49.5295 | 74.2942 | 99.0589 | 123.8236 | 148.5884 | 173.3531 | 198.1178 | 222.8825 | 247.6473
| 95 | 25.5845 | 51.169 | 76.7535 | 102.338 | 127.9225 | 153.5069 | 179.0914 | 204.6759 | 230.2604 | 255.8449
| 96 | 26.4294 | 52.8588 | 79.2882 | 105.7177 | 132.1471 | 158.5765 | 185.0059 | 211.4353 | 237.8647 | 264.2941
| 97 | 27.3003 | 54.6005 | 81.9008 | 109.201 | 136.5013 | 163.8015 | 191.1018 | 218.4021 | 245.7023 | 273.0026
| 98 | 28.1978 | 56.3956 | 84.5934 | 112.7912 | 140.989 | 169.1868 | 197.3846 | 225.5824 | 253.7802 | 281.978
| 99 | 29.1229 | 58.2457 | 87.3686 | 116.4915 | 145.6143 | 174.7372 | 203.86 | 232.9829 | 262.1058 | 291.2286
| 100 | 30.0763 | 60.1526 | 90.2288 | 120.3051 | 150.3814 | 180.4577 | 210.5339 | 240.6102 | 270.6865 | 300.7628

## State Point
Psychrometric Calculations
Inputs
Dry Bulb Temperature | 75 | °F
Wet Bulb Temperature | 60 | °F
Altitude | 2500 | Ft.
Outputs
Atmospheric Pressure | 26.82 | In. Hg | 13.1728 | psi
Vapor Press. at saturation | 0.87505 | In. Hg | 0.42979 | psi
Vapor Pressure | 0.38205 | In. Hg | 0.18765 | psi
Dew Point Temperature | 51.3731 | °F
Relative Humidity | 43.6605 | Percent
Humidity Ratio | 0.0089885 | lb/lb | 62.9193 | grains/lb
Enthalpy | 27.8361 | Btu/lb
Specific Volume | 15.2491 | Ft^3/lb
Shaded | areas are input, all others are calculated.

## Mixing Problem
Psychrometric Calculations
Mixing Problem
Inputs | Air Stream 1 |  | Air Stream 2 |  | Mixed Air
Air Flow Rate | 100 | cfm | 100 | cfm | 200 | cfm
Dry Bulb Temperature | 75 | °F | 96 | °F | 85.5 | °F
Wet Bulb Temperature | 57 | °F | 80 | °F | 69.7 | °F
Altitude | 2500 | Ft.
Outputs
Atmospheric Pressure | 26.82 | In. Hg
Vapor Press. at saturation | 0.87505 | In. Hg | 1.7124 | In. Hg | 1.2331 | In. Hg
Vapor Pressure | 0.30068 | In. Hg | 0.88593 | In. Hg | 0.58566 | In. Hg
Dew Point Temperature | 45.0286 | °F | 75.371 | °F | 63.2274 | °F
Relative Humidity | 34.3617 | Percent | 51.7373 | Percent | 47.4939 | Percent
Humidity Ratio | 0.0070524 | lb/lb | 0.021248 | lb/lb | 0.013984 | lb/lb
| 49.3669 | grains/lb | 148.7362 | grains/lb | 97.8889 | grains/lb
Enthalpy | 25.7175 | Btu/lb | 46.4898 | Btu/lb | 35.8606 | Btu/lb
Specific Volume | 15.2024 | Ft^3/lb | 16.1555 | Ft^3/lb | 15.6691 | Ft^3/lb
Mass Flow Rate, dry air | 6.5779 | lb/min | 6.1898 | lb/min | 12.7677 | lb/min
Mass Flow Rate, water vapor | 0.04639 | lb/min | 0.13152 | lb/min | 0.17791 | lb/min
Mass Flow Rate, moist air | 6.6243 | lb/min | 6.3214 | lb/min | 12.9456 | lb/min
| Shaded | areas are input, all others are calculated.