## 4.WATER COST WCC
ATTACHMENT 4
Project: |  | Replace Community HVAC System - Abqaiq | [6 empty] | Project No: | BI-10-05294
Subject: |  | Water consumption cose for 25 Years Life cycle
REPLACE COMMUNITY HVAC SYSTEMS - ABQAIQ
WATER CONSUMPTION COST FOR 25 YEARS LIFE CYCLE
S.NO | COST ITEM | OPTION 1 WATER COOLED CHILLERS
|  | Year |  | Water flow rate (m3/hr) through cooling towers. | Number of Hours in year | Evaporation rate (%) | Water consumption/Plant (m3/hr) | Total m3 | USD /m3 of water | Total USD
1 | PLANT 1A-Water consumption cost | 1 | 2025 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
2 |  | 2 | 2026 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
3 |  | 3 | 2027 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
4 |  | 4 | 2028 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
5 |  | 5 | 2029 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
6 |  | 6 | 2030 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
7 |  | 7 | 2031 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
8 |  | 8 | 2032 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
9 |  | 9 | 2033 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
10 |  | 10 | 2034 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
11 |  | 11 | 2035 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
12 |  | 12 | 2036 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
13 |  | 13 | 2037 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
14 |  | 14 | 2038 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
15 |  | 15 | 2039 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
16 |  | 16 | 2040 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
17 |  | 17 | 2041 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
18 |  | 18 | 2042 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
19 |  | 19 | 2043 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
20 |  | 20 | 2044 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
21 |  | 21 | 2045 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
22 |  | 22 | 2046 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
23 |  | 23 | 2047 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
24 |  | 24 | 2048 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
25 |  | 25 | 2049 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
| PLANT 1A-Total Water consumption cost for 25 years | [8 empty] | 4777120
1 | PLANT 1B-Water consumption cost | 1 | 2025 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
2 |  | 2 | 2026 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
3 |  | 3 | 2027 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
4 |  | 4 | 2028 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
5 |  | 5 | 2029 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
6 |  | 6 | 2030 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
7 |  | 7 | 2031 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
8 |  | 8 | 2032 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
9 |  | 9 | 2033 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
10 |  | 10 | 2034 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
11 |  | 11 | 2035 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
12 |  | 12 | 2036 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
13 |  | 13 | 2037 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
14 |  | 14 | 2038 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
15 |  | 15 | 2039 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
16 |  | 16 | 2040 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
17 |  | 17 | 2041 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
18 |  | 18 | 2042 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
19 |  | 19 | 2043 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
20 |  | 20 | 2044 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
21 |  | 21 | 2045 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
22 |  | 22 | 2046 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
23 |  | 23 | 2047 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
24 |  | 24 | 2048 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
25 |  | 25 | 2049 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
| PLANT 1B-Total Water consumption cost for 25 years | [8 empty] | 7165680
1 | PLANT 2-Water consumption cost | 1 | 2025 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
2 |  | 2 | 2026 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
3 |  | 3 | 2027 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
4 |  | 4 | 2028 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
5 |  | 5 | 2029 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
6 |  | 6 | 2030 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
7 |  | 7 | 2031 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
8 |  | 8 | 2032 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
9 |  | 9 | 2033 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
10 |  | 10 | 2034 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
11 |  | 11 | 2035 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
12 |  | 12 | 2036 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
13 |  | 13 | 2037 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
14 |  | 14 | 2038 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
15 |  | 15 | 2039 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
16 |  | 16 | 2040 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
17 |  | 17 | 2041 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
18 |  | 18 | 2042 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
19 |  | 19 | 2043 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
20 |  | 20 | 2044 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
21 |  | 21 | 2045 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
22 |  | 22 | 2046 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
23 |  | 23 | 2047 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
24 |  | 24 | 2048 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
25 |  | 25 | 2049 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
| PLANT 2-Total Water consumption cost for 25 years | [8 empty] | 4777120
1 | PLANT 3-Water consumption cost | 1 | 2025 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
2 |  | 2 | 2026 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
3 |  | 3 | 2027 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
4 |  | 4 | 2028 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
5 |  | 5 | 2029 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
6 |  | 6 | 2030 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
7 |  | 7 | 2031 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
8 |  | 8 | 2032 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
9 |  | 9 | 2033 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
10 |  | 10 | 2034 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
11 |  | 11 | 2035 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
12 |  | 12 | 2036 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
13 |  | 13 | 2037 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
14 |  | 14 | 2038 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
15 |  | 15 | 2039 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
16 |  | 16 | 2040 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
17 |  | 17 | 2041 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
18 |  | 18 | 2042 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
19 |  | 19 | 2043 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
20 |  | 20 | 2044 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
21 |  | 21 | 2045 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
22 |  | 22 | 2046 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
23 |  | 23 | 2047 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
24 |  | 24 | 2048 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
25 |  | 25 | 2049 | 1227 | 2920 | 1 | 12.27 | 35828.4 | 1.6 | 286627.2
| PLANT 3-Total Water consumption cost for 25 years | [8 empty] | 7165680
1 | PLANT 4-Water consumption cost | 1 | 2025 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
2 |  | 2 | 2026 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
3 |  | 3 | 2027 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
4 |  | 4 | 2028 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
5 |  | 5 | 2029 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
6 |  | 6 | 2030 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
7 |  | 7 | 2031 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
8 |  | 8 | 2032 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
9 |  | 9 | 2033 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
10 |  | 10 | 2034 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
11 |  | 11 | 2035 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
12 |  | 12 | 2036 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
13 |  | 13 | 2037 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
14 |  | 14 | 2038 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
15 |  | 15 | 2039 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
16 |  | 16 | 2040 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
17 |  | 17 | 2041 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
18 |  | 18 | 2042 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
19 |  | 19 | 2043 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
20 |  | 20 | 2044 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
21 |  | 21 | 2045 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
22 |  | 22 | 2046 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
23 |  | 23 | 2047 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
24 |  | 24 | 2048 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
25 |  | 25 | 2049 | 818 | 2920 | 1 | 8.18 | 23885.6 | 1.6 | 191084.8
| PLANT 4-Total Water consumption cost for 25 years | [8 empty] | 4777120

## Cooling Tower - Make Up Water
Project Name | : Microsoft Building |  |  |  | Computed by: | MIA
Location | : Narnia |  |  |  | Checked by: | SSK
Equipment | CT - 01 |  |  |  | Approved by: | AMK
COOLING TOWER - MAKE UP WATER CALCULATION
[7 empty] | Website | : | https://www.hvacsimplified.in
[7 empty] | YouTube | : | https://www.youtube.com/c/HVACSimplifiedOnlineTrainingByAMK/featured
[7 empty] | Email | : | info@hvacsimplified.in
[7 empty] | Instagram | : | https://www.instagram.com/hvac_simplified/
[7 empty] | LinkedIn | : | https://www.linkedin.com/company/hvac-simplified/?viewAsMember=true
[7 empty] | Facebook | : | https://m.facebook.com/HVAC.SIMPLIFIED/?ref=bookmarks
Cooling Tower Make-Up Water Calculations (ASHRAE DCG)
| S.NO | PARAMETER |  |  | DATA
| A | INPUT DATA
| 1 | Water flow rate | Q | m3/h | 409
| 2 | Cycle of concentration | C | C | 4
| 3 | Inlet temperature of water | ti | deg C | 35
| 4 | Outlet temperature of water | to | deg C | 29.4444
| B | OUTPUT DATA
| 5 | Tower temperature range(deg C) | ∆T | ti-to | 5.5556
| 6 | Evaporation (m3/h) | E | 0.0014 x Q x ∆T | 3.1811
| 7 | Drift loss (m3/h) | D | 0.0002 x Q | 0.0818
| 8 | Blow down (m3/h) | B | E - [(C-1) X D] /(C-1) | 0.97858
|  | Total amount of make up water (m3/h) | m3/h | E + D + B | 4.2415