## 1. Office
🏢 OFFICE — ASHRAE 62.1 FRESH AIR CALCULATION
Typical Open-Plan / Enclosed Office Space
Breathing Zone Outdoor Airflow — ASHRAE 62.1 Ventilation Rate Procedure
Vbz = Rp × Pz + Ra × Az
| Rp = outdoor airflow rate per person (L/s·person) |  | Pz = zone population (persons)
| Ra = outdoor airflow rate per unit area (L/s·m²) |  | Az = zone floor area (m²)
Typical office: workstations, private offices, meeting rooms — low-to-moderate occupant density, area-driven outdoor air load.
GIVEN — INPUT VALUES (yellow cells are editable)
| Parameter | Symbol | Value | Unit | Description
| Zone Floor Area | Az | 200 | m² | Net occupied floor area of the space
| Zone Population | Pz | 20 | persons | Expected number of occupants
| People Outdoor Air Rate | Rp | 2.5 | L/s·person | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
| Area Outdoor Air Rate | Ra | 0.3 | L/s·m² | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
CALCULATION
| Step | Formula | Result | Unit | Notes
| People component | Rp × Pz | 50 | L/s | Outdoor air for occupants
| Area component | Ra × Az | 60 | L/s | Outdoor air for building/area sources
| Breathing Zone Airflow | Vbz = Rp×Pz + Ra×Az | 110 | L/s | Minimum required outdoor airflow
| Convert to CFM | Vbz(L/s) × 2.119 | 233.09 | CFM | 1 L/s = 2.119 CFM
OFFICE Fresh Air Required = 110 L/s ≈ 233 CFM
💡 Insight: Area load contributes strongly in offices — the low occupant density means Ra×Az can rival or exceed the people component.
ASHRAE 62.1 TABLE 6-1 — REFERENCE DEFAULT VALUES (for verification)
| Occupancy Category | Rp (L/s·person) | Ra (L/s·m²) | Default Density | Source
| Office space | 2.5 | 0.3 | 5 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
| Reception areas | 2.5 | 0.3 | 30 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
| Conference/meeting | 2.5 | 0.3 | 50 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
📘 More free HVAC calculators, design notes & solved examples: www.hvacsimplified.in
▶ Watch full HVAC design tutorials — search “HVAC Simplified by AMK” on YouTube

## 2. Classroom
🏫 CLASSROOM — ASHRAE 62.1 FRESH AIR CALCULATION
Typical K-12 / University Classroom
Breathing Zone Outdoor Airflow — ASHRAE 62.1 Ventilation Rate Procedure
Vbz = Rp × Pz + Ra × Az
| Rp = outdoor airflow rate per person (L/s·person) |  | Pz = zone population (persons)
| Ra = outdoor airflow rate per unit area (L/s·m²) |  | Az = zone floor area (m²)
Typical classroom: rows of student desks facing an instructor — high occupant density drives the outdoor air requirement.
GIVEN — INPUT VALUES (yellow cells are editable)
| Parameter | Symbol | Value | Unit | Description
| Zone Floor Area | Az | 100 | m² | Net occupied floor area of the space
| Zone Population | Pz | 30 | persons | Expected number of occupants
| People Outdoor Air Rate | Rp | 5 | L/s·person | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
| Area Outdoor Air Rate | Ra | 0.6 | L/s·m² | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
CALCULATION
| Step | Formula | Result | Unit | Notes
| People component | Rp × Pz | 150 | L/s | Outdoor air for occupants
| Area component | Ra × Az | 60 | L/s | Outdoor air for building/area sources
| Breathing Zone Airflow | Vbz = Rp×Pz + Ra×Az | 210 | L/s | Minimum required outdoor airflow
| Convert to CFM | Vbz(L/s) × 2.119 | 444.99 | CFM | 1 L/s = 2.119 CFM
CLASSROOM Fresh Air Required = 210 L/s ≈ 445 CFM
💡 Insight: High occupant density drives outdoor air demand in classrooms — the people component (Rp×Pz) typically dominates Vbz.
ASHRAE 62.1 TABLE 6-1 — REFERENCE DEFAULT VALUES (for verification)
| Occupancy Category | Rp (L/s·person) | Ra (L/s·m²) | Default Density | Source
| Classrooms (age 9 plus) | 5 | 0.6 | 35 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
| Classrooms (age 5–8) | 5 | 0.6 | 25 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
| Lecture hall (fixed seats) | 3.8 | 0.3 | 150 persons/100 m² | ASHRAE 62.1-2019, Table 6-1
📘 More free HVAC calculators, design notes & solved examples: www.hvacsimplified.in
▶ Watch full HVAC design tutorials — search “HVAC Simplified by AMK” on YouTube

## 3. Hospital
🏥 HOSPITAL ROOM — ASHRAE 62.1 FRESH AIR CALCULATION
Typical Inpatient / Patient Room
Breathing Zone Outdoor Airflow — ASHRAE 62.1 Ventilation Rate Procedure
Vbz = Rp × Pz + Ra × Az
| Rp = outdoor airflow rate per person (L/s·person) |  | Pz = zone population (persons)
| Ra = outdoor airflow rate per unit area (L/s·m²) |  | Az = zone floor area (m²)
Typical patient room: bed, monitoring equipment, visitor chair — requires elevated, continuously filtered outdoor air.
GIVEN — INPUT VALUES (yellow cells are editable)
| Parameter | Symbol | Value | Unit | Description
| Zone Floor Area | Az | 40 | m² | Net occupied floor area of the space
| Zone Population | Pz | 4 | persons | Expected number of occupants
| People Outdoor Air Rate | Rp | 7.5 | L/s·person | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
| Area Outdoor Air Rate | Ra | 0.9 | L/s·m² | Per ASHRAE 62.1 Table 6-1 (occupancy category default)
CALCULATION
| Step | Formula | Result | Unit | Notes
| People component | Rp × Pz | 30 | L/s | Outdoor air for occupants
| Area component | Ra × Az | 36 | L/s | Outdoor air for building/area sources
| Breathing Zone Airflow | Vbz = Rp×Pz + Ra×Az | 66 | L/s | Minimum required outdoor airflow
| Convert to CFM | Vbz(L/s) × 2.119 | 139.854 | CFM | 1 L/s = 2.119 CFM
HOSPITAL ROOM Fresh Air Required = 66 L/s ≈ 140 CFM
💡 Insight: Hospitals often need extra ventilation and pressure control beyond the basic Vbz result — always cross-check against ASHRAE 170.
ASHRAE 62.1 TABLE 6-1 — REFERENCE DEFAULT VALUES (for verification)
| Occupancy Category | Rp (L/s·person) | Ra (L/s·m²) | Default Density | Source
| Patient room (per 62.1 — similar-occupancy estimate) | 2.5 | 0.3 | — | 62.1 Note 6 / Interp. IC 62.1-2013-1
| Patient room — min. total ACH | 6 ACH (total) | — | — | ASHRAE 170-2021, Table 7.1
| Patient room — min. outdoor ACH | 2 ACH (outdoor) | — | — | ASHRAE 170-2021, Table 7.1
⚠ Design note: ASHRAE 62.1's Table 6-1 does not include health-care occupancies — the interpretation letter IC 62.1-2013-1 confirms that ASHRAE/ASHE Standard 170 (Ventilation of Health-Care Facilities) governs patient rooms, using an air-changes-per-hour (ACH) method (typically 2 ACH outdoor air, 6 ACH total) rather than the per-person Vbz method shown above. The Rp/Ra values used in this sheet are illustrative, for learning the Ventilation Rate Procedure only — verify final patient-room design against ASHRAE 170 and local code.
📘 More free HVAC calculators, design notes & solved examples: www.hvacsimplified.in
▶ Watch full HVAC design tutorials — search “HVAC Simplified by AMK” on YouTube