## Smoke Extraction Calc
BASEMENT SMOKE EXTRACTION: ONE COMPLETE CALCULATION FROM ACH TO FAN SELECTION
Step-by-Step Engineering Example ¦ Life Safety First. Design Right. ¦ Remove Smoke • Protect Lives • Ensure Safe Egress.
1. BASEMENT DETAILS (DESIGN INPUT) |  |  | 2. VOLUME CALCULATION |  | 4. BASEMENT SECTION DIAGRAM (TYPICAL)
Building | Commercial (Office + Parking) |  | Formula | V = L × W × H
Basement type | 2 underground levels |  | Volume, V (m³) | 7200
Selected level | B1 (for calculation)
Length, L (m) | 60 |  | 3. REQUIRED SMOKE EXTRACTION FLOW
Width, W (m) | 40 |  | Formula | Q = ACH × Volume
Clear height, H (m) | 3 |  | Required flow, Q (m³/hr) | 72000
Usage | Car parking |  | Required flow, Q (m³/s) | 20
Design standard | NBC 2016 / IS 1643 / NFPA 92 |  | Required flow, Q (CFM) | 42377.64
Design method | Air Changes per Hour (ACH)
Required ACH (per hr) | 10
5. DUCT SIZE CALCULATION (MAIN RISER) |  |  | 6. DUCT SIZE FOR BRANCH (FROM ZONE) |  | 7. SYSTEM RESISTANCE (PRESSURE LOSS)
Design velocity (m/s) | 10 |  | No. of smoke extraction shafts | 2 | Duct friction loss (~50 m total), Pa | 250
Flow, Q (m³/s) | 20 |  | Flow per shaft (m³/hr) | 36000 | Bends, transitions, fittings, Pa | 150
Required area, A (m²) | 2 |  | Flow per shaft (m³/s) | 10 | Fire damper / motorized damper, Pa | 100
Aspect ratio (W : H) | 1.5 |  | Branch design velocity (m/s) | 10 | Louvre / outlet loss, Pa | 100
Calculated height (m) | 1.1547 |  | Required branch area (m²) | 1 | Safety factor (10–20%), Pa | 100
Calculated width (m) | 1.7321 |  | Adopted branch width (mm) | 1000 | Total External Static Pressure, ESP (Pa) | 700
Adopted duct width (mm) | 1800 |  | Adopted branch height (mm) | 1000
Adopted duct height (mm) | 1200 |  | Adopted branch area (m²) | 1
Adopted area (m²) | 2.16 |  | Actual branch velocity (m/s) | 10
Actual velocity (m/s) | 9.2593
8. FAN SELECTION |  |  | 9. ACH VERIFICATION |  | 11. PLAN VIEW (SCHEMATIC)
Required flow per fan (m³/hr) | 36000 |  | Target ACH | 10
Required flow per fan (CFM) | 21188.82 |  | Actual ACH (Q / Volume) | 10
Required ESP (Pa) | 700 |  | Check | OK ✓
Fan type | Axial / Mixed Flow Smoke Exhaust Fan
Fire rating | 400°C for 2 hours (as per NBC / IS 1643) |  | 10. SMOKE EXTRACTION STRATEGY
Number of fans (duty + standby) | 2 |  | Shaft strategy | Provide 2 shafts, 50% capacity each
Arrangement | 2 x 50% (duty / standby) |  | Control | Automatic operation on fire alarm
Drive | Direct / Belt (as per manufacturer) |  | Interlock | Interlocked with basement pressurization (for staircases)
Accessories | Vibration isolators, flexible connector, motorized damper, weather louvre |  | Make-up air | Provide fresh air make-up from natural openings or mechanical supply
12. KEY STANDARDS & GUIDELINES |  |  | 13. FINAL SUMMARY |  | 14. IMPORTANT NOTES
Standard 1 | NBC 2016 – Part 4 (Fire & Life Safety) |  | Basement volume (m³) | 7200 | Note 1 | ACH requirement may vary based on local codes, building use and fire strategy.
Standard 2 | IS 1643 – Code of Practice for Fire Safety of Buildings |  | Required smoke flow (m³/hr) | 72000 | Note 2 | Consider make-up air for effective smoke extraction.
Standard 3 | NFPA 92 – Smoke Control Systems |  | Required ACH | 10 | Note 3 | Coordinate with architectural, structural and MEP services.
Standard 4 | SMACNA – Duct Design Guidelines |  | Main duct size (mm) | 1800 x 1200 | Note 4 | Provide independent power supply for smoke extraction fans.
Standard 5 | Manufacturer datasheets (fan performance) |  | Branch duct size (mm, per shaft) | 1000 x 1000 | Note 5 | Verify final selection with manufacturer's performance curve.
|  |  | Fan selection | 2 x 36,000 m³/hr @ 700 Pa | Note 6 | This is a typical example. Modify as per project requirements and applicable standards.
|  |  | Fan rating | 400°C for 2 hours
|  |  | Arrangement | 50% duty + 50% standby
Codes & Standards Reference: NBC 2016 – Part 4 (Fire & Life Safety) ¦ IS 1643 – Code of Practice for Fire Safety of Buildings ¦ NFPA 92 – Smoke Control Systems ¦ SMACNA – Duct Design Guidelines
www.hvacsimplified.in ¦ © HVAC Simplified™ — Safe Spaces. Smart Engineering. Stronger Tomorrows. ¦ All values are a typical worked example — verify against project-specific design criteria and local code requirements.
Correction applied: Section 3's flow-to-CFM conversion has been corrected (see cell comment on the CFM result) — CFM = Q(m³/s) × 60 × 35.3147.
Legend: | Editable input | Calculated
Note on J14: Corrected conversion. The original hand-calc divided by 3600 and labelled the result 'CFM', which is actually ft³/s (706 ft³/s), understating true CFM by 60x. Correct relation: 1 m³/hr = 0.588578 CFM, so CFM = Q(m³/s) x 60 x 35.3147.