## BUILDING
PUMP HEAD CALCULATION SHEET
Project name: | [8 empty] | Pages |  | of
DATE
Project No. |  |  |  |  | REVISION |  |  |  | ENGINEER
Consultant: | [9 empty] | PIPE CONSTRUCTION
Supplier: | [9 empty] | Medium Steel Pipe
Designation
Location: | [12 empty] | Building flow | 275 | worst case
|  | l/s |  | KPa |  |  |  | l/s |  |  | KPa
Spec duty |  | 20 |  |  |  | Actual |  |  |  |  | 170 |  | 56.874 | ft
|  |  | PIPE |  |  | LENGTH. OR | PRESS | No. | TOTAL | PROGRESSIVE
DESCRIPTION |  | SECT | SIZE | FLOW | VEL | EQUIVALENT | DROP | OFF | P.D | PRESS. DROP | REMARKS | Flow
/ ITEM |  | -ION | mm | l/s | m/s | m | kPa/m |  | kPa | kPa |  | GPM
Inside Mech. Room | SUPPLY
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 1.2 | 0.12749 | 1 | 0.15299 |  | F Horizontal pipe | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1389 | 2.06 | 0.12749 | 1 | 0.26263 |  | F - Bend to pipe header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 0.5 | 0.12749 | 1 | 0.063746 |  | F - Horizontal Pipe | 137
Tee - Line |  | A | 100 | 8.6433 | 1.1389 | 2.44 | 0.12749 | 1 | 0.31108 |  | F - Bend to pipe header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 2 | 0.12749 | 1 | 0.25499 |  | F - To pump suction | 137
Isolation Valve | PUMP | A | 100 | 8.6433 | 1.1389 | 1.37 | 0.12749 | 1 | 0.17466 |  | F - Isolation Valve | 137
Strainer |  | A | 100 | 8.6433 | 1.1389 |  | 0.12749 | 1 | 15 |  | F - Strainer | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 5 | 0.12749 | 1 | 0.63746 |  | F - From pump discharge to Header | 137
Non Return Valve |  | A | 100 | 8.6433 | 1.1389 | 12.1 | 0.12749 | 1 | 1.5427 |  | F - From pump discharge | 137
Isolation Valve |  | A | 100 | 8.6433 | 1.1389 | 1.37 | 0.12749 | 1 | 0.17466 |  | F - From pump discharge | 137
Straight pipe | SUPPLY | A | 100 | 8.6433 | 1.1389 | 0.5 | 0.12749 | 1 | 0.063746 |  | F - to discharge header | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1389 | 2.06 | 0.12749 | 1 | 0.26263 |  | F - Bend to pipe header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 1 | 0.12749 | 1 | 0.12749 |  | F - Vertical pipe exiting ground | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1389 | 2.06 | 0.12749 | 1 | 0.26263 |  | F - Bend to pipe header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 0.5 | 0.12749 | 1 | 0.063746 |  | F - horizontal pipe exiting ground | 137
Tee - Branch |  | A | 100 | 8.6433 | 1.1389 | 6.4 | 0.12749 | 1 | 0.81595 |  | F - Tee to main header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 0.5 | 0.12749 | 1 | 0.063746 |  | F - Horizontal pipe | 137
90 R Bend |  | A | 100 | 8.6433 | 1.1389 | 2.06 | 0.12749 | 1 | 0.26263 |  | F - Bend to pipe header | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 0.5 | 0.12749 | 1 | 0.063746 |  | F - Horizontal Pipe | 137
Air Dirt Separator |  | A | 100 | 8.6433 | 1.1389 |  | 0.12749 | 1 | 5 |  | F - Air dirt separator | 137
Straight pipe |  | A | 100 | 8.6433 | 1.1389 | 3.3 | 0.12749 | 1 | 0.42073 |  | F & R - Vertical pipe exiting ground | 137
Tee - Branch |  | A | 100 | 8.6433 | 1.1389 | 6.4 | 0.12749 | 1 | 0.81595 |  | F - Tee to main header | 137
Straight pipe | RETURN | A | 100 | 14.8892 | 1.9619 | 3.4 | 0.34907 | 1 | 1.1868 |  | R - Horizontal Pipe to HEX header | 236
90 R Bend |  | A | 100 | 14.8892 | 1.9619 | 2.06 | 0.34907 | 1 | 0.71908 |  | R - Bend to pipe header | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9619 | 3.4 | 0.34907 | 1 | 1.1868 |  | R - Horizontal Pipe to header | 236
90 R Bend |  | A | 100 | 14.8892 | 1.9619 | 2.06 | 0.34907 | 1 | 0.71908 |  | R- Bend to pipe header | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9619 | 7 | 0.34907 | 1 | 2.4435 |  | R - Horizontal Pipe to HEX header | 236
Tee - Branch |  | A | 100 | 14.8892 | 1.9619 | 6.4 | 0.34907 | 1 | 2.234 |  | F & R - header take off | 236
Straight pipe |  | A | 100 | 14.8892 | 1.9619 | 5 | 0.34907 | 1 | 1.7453 |  | F - To pump suction | 236
Tee - Branch |  | A | 100 | 5.6781 | 0.74818 | 6.4 | 0.058551 | 1 | 0.37473 |  | F - to discharge header | 90
Straight pipe | F & R | A | 80 | 5.6781 | 1.3604 | 3 | 0.25434 | 2 | 1.526 |  | F & R - straight pipe inside plantroom | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3604 | 1.52 | 0.25434 | 2 | 0.77319 |  | F &R - Bends inside Mech room | 90
Straight pipe |  | A | 80 | 5.6781 | 1.3604 | 7 | 0.25434 | 2 | 3.5608 |  | F & R - Return inside Mech room | 90
Isolation Valve |  | A | 80 | 5.6781 | 1.3604 | 0.97 | 0.25434 | 2 | 0.49342 |  | F & R- Isolation Valve | 90
Straight pipe |  | A | 80 | 5.6781 | 1.3604 | 1 | 0.25434 | 2 | 0.50868 |  | F & R - Return inside Mech room | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3604 | 1.52 | 0.25434 | 2 | 0.77319 | 45.0426 | F & R - Bends inside Mech room to upper | 90 | 15.0691 | ft
45.0426
Inside building
Straight pipe |  | A | 80 | 5.6781 | 1.3604 | 40 | 0.25434 | 2 | 20.3472 |  | F & R - length of 5" pipework | 90
90 R Bend |  | A | 80 | 5.6781 | 1.3604 | 1.52 | 0.25434 | 7 | 2.7062 |  | F & R - bends of 5" pipework | 90
Isolation Valve |  | A | 80 | 5.6781 | 1.3604 | 0.97 | 0.25434 | 2 | 0.49342 |  | F - isolation into apartment | 90
Tee - Branch |  | A | 80 | 3.8819 | 0.93004 | 4.57 | 0.12576 | 2 | 1.1495 |  | F & R - T lines of 5" pipework | 61.53
Tee - Line |  | A | 80 | 0.25236 | 0.060461 | 1.54 | 0.00079648 | 3 | 0.0036797 |  | F & R - T lines of 5" pipework | 4
Tee - Line |  | A | 80 | 0.13943 | 0.033405 | 1.54 | 0.00026544 | 2 | 0.00081757 |  | F & R - T lines of 5" pipework | 2.21
Straight pipe |  | A | 80 | 3.8819 | 0.93004 | 3.5 | 0.12576 | 2 | 0.88033 |  | F & R - length of 5" pipework | 61.53
Straight pipe |  | A | 80 | 3.6296 | 0.86958 | 2 | 0.11104 | 2 | 0.44416 |  | F & R - length of 5" pipework | 57.53
Straight pipe |  | A | 80 | 3.4901 | 0.83618 | 3 | 0.10327 | 2 | 0.61962 |  | F & R - length of 5" pipework | 55.32
Straight pipe |  | A | 80 | 3.0983 | 0.74231 | 4 | 0.082833 | 2 | 0.66267 |  | F & R - length of 5" pipework | 49.11
Reducer |  | A | 65 | 2.846 | 0.97065 | 0.85 | 0.16942 | 2 | 0.28801 |  | F & R - Reducer 5" to 4" | 45.11
Straight pipe |  | A | 80 | 2.846 | 0.68185 | 1 | 0.070774 | 2 | 0.14155 |  | F & R - length of 5" pipework | 45.11
Straight pipe |  | A | 80 | 2.7066 | 0.64844 | 1 | 0.064486 | 2 | 0.12897 |  | F & R - length of 5" pipework | 42.9
Balance valve |  | A | 65 | 2.7066 | 0.92309 |  | 0.15437 | 2 | 3 |  | R - balance into apartment | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 1 | 0.15437 | 2 | 0.30873 |  | F & R - length of 4" pipework | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92309 | 1.35 | 0.15437 | 2 | 0.41679 |  | F & R - bends of 4" pipework | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 1.5 | 0.15437 | 2 | 0.4631 |  | F & R - length of 4" pipework | 42.9
Tee - Branch |  | A | 65 | 2.3495 | 0.80131 | 3.65 | 0.11878 | 2 | 0.86712 |  | F & R - Horizontal | 37.24
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 1 | 0.15437 | 2 | 0.30873 |  | F & R - length of 4" pipework | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92309 | 1.35 | 0.15437 | 2 | 0.41679 |  | F & R - bends of 4" pipework | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 1 | 0.15437 | 2 | 0.30873 |  | F & R - length of 4" pipework | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92309 | 1.35 | 0.15437 | 2 | 0.41679 |  | F & R - bends of 4" pipework | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 3.5 | 0.15437 | 2 | 1.0806 |  | F & R - Vertical pipework to retail | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92309 | 1.35 | 0.15437 | 2 | 0.41679 |  | F & R Vertical elbow at level 0 | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 0.5 | 0.15437 | 2 | 0.15437 |  | F & R - Vertical pipework to retail | 42.9
90 R Bend |  | A | 65 | 2.7066 | 0.92309 | 1.35 | 0.15437 | 2 | 0.41679 |  | F & R horizontal elbow at level 0 | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 0.5 | 0.15437 | 2 | 0.15437 |  | F & R - Vertical pipework at retail | 42.9
Tee - Branch |  | A | 65 | 2.7066 | 0.92309 | 3.65 | 0.15437 | 2 | 1.1269 |  | F & R - Horizontal pipework to retail | 42.9
Straight pipe |  | A | 65 | 2.7066 | 0.92309 | 0.5 | 0.15437 | 2 | 0.15437 |  | F & R - Horizontal pipework to retail | 42.9
Tee - Branch |  | A | 50 | 1.8649 | 1.0136 | 3.04 | 0.24093 | 2 | 1.4649 |  | F & R - Horizontal pipework to retail | 29.56
Straight pipe |  | A | 65 | 1.8649 | 0.63605 | 4.3 | 0.077444 | 2 | 0.66602 |  | F & R - Horizontal pipework to retail | 29.56
Tee - Line |  | A | 40 | 0.40378 | 0.40338 | 0.79 | 0.063183 | 2 | 0.099829 |  | F & R - Horizontal pipework to retail | 6.4
Straight pipe |  | A | 65 | 1.4612 | 0.49834 | 8.5 | 0.049288 | 2 | 0.83789 |  | F & R - Horizontal pipework to retail | 23.16
Tee - Line |  | A | 40 | 0.40378 | 0.40338 | 0.79 | 0.063183 | 2 | 0.099829 |  | F & R - Horizontal pipework to retail | 6.4
Straight pipe |  | A | 65 | 0.80755 | 0.27542 | 9.5 | 0.016436 | 2 | 0.31228 |  | F & R - Horizontal pipework to retail | 12.8
Tee - Line |  | A | 40 | 0.40378 | 0.40338 | 0.79 | 0.063183 | 2 | 0.099829 |  | F & R - Horizontal pipework to retail | 6.4
Reducer |  | A | 40 | 0.40378 | 0.40338 | 0.53 | 0.063183 | 2 | 0.066974 |  | F & R - Horizontal pipework to retail | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.40338 | 9 | 0.063183 | 2 | 1.1373 |  | F & R - Horizontal pipework to retail | 6.4
90 R Bend |  | A | 65 | 0.40378 | 0.13771 | 1.35 | 0.0045529 | 2 | 0.012293 |  | F & R - Horizontal bends to retail | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.40338 | 9 | 0.063183 | 2 | 1.1373 |  | F & R - Horizontal pipework to retail | 6.4
90 R Bend |  | A | 65 | 0.40378 | 0.13771 | 1.35 | 0.0045529 | 2 | 0.012293 |  | F & R - Horizontal bends to retail | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.40338 | 9 | 0.063183 | 2 | 1.1373 |  | F & R - Horizontal pipework to retail | 6.4
Straight pipe |  | A | 40 | 0.40378 | 0.40338 | 9 | 0.063183 | 2 | 1.1373 | 46.0983 |  | 6.4 | 15.4223 | ft
91.1409
Index AHU
Strainer |  | A | 40 | 0.40378 | 0.40338 |  | 0.063183 | 1 | 15 |  | F - Coil Strainer | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.40338 | 0.53 | 0.063183 | 1 | 0.033487 |  | F - Isolation valve | 6.4
Cooling coil |  | A | 40 | 0.40378 | 0.40338 |  | 0.063183 | 1 | 20 |  | COOLING COIL | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.40338 | 0.53 | 0.063183 | 1 | 0.033487 |  | R - Isolation valve 1 | 6.4
Tee - Line |  | A | 40 | 0.40378 | 0.40338 | 0.79 | 0.063183 | 1 | 0.049914 |  | R - Bypass takeoff | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.40338 | 0.53 | 0.063183 | 1 | 0.033487 |  | R - Isolation valve 2 | 6.4
Control Valve |  | A | 40 | 0.40378 | 0.40338 |  | 0.063183 | 1 | 20 |  | COIL CONTROL VALVE | 6.4
Isolation Valve |  | A | 40 | 0.40378 | 0.40338 | 0.53 | 0.063183 | 1 | 0.033487 |  | R - Isolation valve 2 | 6.4
Tee - Line |  | A | 40 | 0.40378 | 0.40338 | 0.79 | 0.063183 | 1 | 0.049914 |  | R - Bypass takeoff | 6.4
Balance valve |  | A | 40 | 0.40378 | 0.40338 |  | 0.063183 | 1 | 5 | 60.2338 | R - line balance valve | 6.4 | 20.1514 | ft
[10 empty] | 151.3747 |  |  | 50.6428 | ft
[5 empty] | SUB-TOTAL |  |  |  | 151.3747
NOTES: |  |  |  |  | SAFETY |  | 10% |  | 15.1375
[5 empty] | TOTAL P.D |  | kPa |  | 166.5121
[8 empty] | SUPPLIER |  |  | MODEL No.
MODEL SPECIFIED
MODEL SELECTED
Note on A12: ONLY ONE FITTING OR STRAIGHT LENGTH PER LINE. NOT BOTH !!
Note on I13: Pressure-drop gradient calculated with the Hazen-Williams equation (SI units), using the pipe schedule table on the Data sheet (columns Q:S). Formula reproduces the workbook's original PipePressureDrop() VBA function exactly, but no longer requires macros to be enabled.
Note on J10: Actual pump duty flow (l/s) not yet entered in the original workbook. Enter the confirmed pump/circuit design flow here once the pipework layout and secondary pumping arrangement are finalised.

## Data
size | B90 | IV | TeeLine | TeeBend | Reducer | Non Ret. | Reducer 1/2 | Check Vlv | Strainer |  | KV | Valve Size | Nominal (mm) | Internal Dia (mm) | Hazen-Williams C
15 | 0.3 | 0.21 | 0.3 | 0.92 | 0.21 | 1.9 | 0.25 | 0.9 | 15 | 61.188 | 0.16 | 15 | 15 | 10.9 | 139
20 | 0.42 | 0.27 | 0.42 | 1.26 | 0.27 | 2.15 | 0.4 | 1.6 | 20 | 19.638 | 0.25 | 15 | 20 | 17 | 140
25 | 0.54 | 0.3 | 0.51 | 1.52 | 0.3 | 3 | 0.46 | 1.8 | 25 | 7.875 | 0.4 | 15 | 25 | 23 | 141
32 | 0.71 | 0.46 | 0.7 | 2.1 | 0.46 | 4.26 | 0.66 | 2.07 | 32 | 2.85 | 0.63 | 15 | 32 | 29.3 | 142
40 | 0.79 | 0.53 | 0.79 | 2.44 | 0.53 | 4.9 | 0.8 | 3.05 | 40 | 1.45 | 1 | 15 | 40 | 35.7 | 143
50 | 1 | 0.7 | 1 | 3.04 | 0.7 | 6 | 0.98 | 4.2 | 50 | 0.5365 | 1.6 | 15 | 50 | 48.4 | 144
65 | 1.35 | 0.85 | 1.29 | 3.65 | 0.85 | 7.6 | 1.3 | 5.2 | 65 | 0.25 | 2.5 | 15 | 65 | 61.1 | 144
80 | 1.52 | 0.97 | 1.54 | 4.57 | 0.97 | 9.2 | 1.5 | 6.2 | 80 | 0.1118 | 4 | 15 | 80 | 72.9 | 145
100 | 2.06 | 1.37 | 2.44 | 6.4 | 1.37 | 12.1 | 2 | 8.2 | 100 | 0.034 | 6.3 | 20 | 100 | 98.3 | 146
125 | 2.32 | 1.84 | 2.58 | 7.62 | 1.84 | 15.2 | 2.5 | 10.2 | 125 | 0.015 | 10 | 25 | 125 | 123.7 | 146
150 | 3 | 2.13 | 3.1 | 9.2 | 2.13 | 18.2 | 3 | 12.8 | 150 | 0.0045 | 16 | 32 | 150 | 148.3 | 146
200 | 3.9 | 2.74 | 4 | 12.2 | 2.74 | 24.4 | 4 | 17 | 200 | 0.00145 | 25 | 40 | 200 | 202.7 | 141
250 | 4.9 | 3.68 | 4.9 | 15.4 | 3.68 | 30.7 | 5 | 21 |  |  | 40 | 50 | 250 | 254.5 | 141
300 | 5.8 | 3.98 | 5.8 | 18.5 | 3.98 | 36.9 | 5.8 | 24.5 |  |  | 63 | 65 | 300 | 303.3 | 141
350 | 7 | 4.8 | 7 | 20.7 | 5.4 | 41.5 | 7 | 29 |  |  | 100 | 80 | 350 | 333.3 | 141
400 | 7.9 | 5.4 | 7.9 | 23.3 | 6 | 46.15 | 7.6 | 33 |  |  | 160 | 100 | 400 | 381 | 141
450 | 8.84 | 6 | 8.8 | 26 | 7 | 50.76 | 8.8 | 37 |  |  | 250 | 125 | 450 | 428.5 | 141
500 | 10.1 | 6.5 | 10.1 | 30.4 | 7.5 | 61.53 | 9.5 | 41 |  |  | 400 | 150 | 500 | 477.9 | 141
550 | 11.1 | 7.4 | 11.1 | 32.5 | 8.4 | 68 | 11 | 45 |  |  |  |  | 550 | 527 | 141
600 | 12.2 | 8 | 12.2 | 35.1 | 9 | 73.84 | 12 | 48 |  |  |  |  | 600 | 574.6 | 141
|  | 3 | 4 | 5 | 6 | 7 | 6
[5 empty] | ecc |  | conc
Note on Q1: Native pipe-schedule reference table (nominal size, internal diameter, Hazen-Williams C) reproduced from the workbook's original VBA functions (FluidVel / PipePressureDrop, © 1999 Cameron Robbins) so velocity and pressure-drop results no longer depend on macros being enabled.

## Vel Head loss
| L/S | 20.24
| Suction | 80 | mm |  | VH loss | 1.0709 | meters
| Discharge | 65 | mm |  | VH loss | 10.5058 | Kpa
|  | Q | N | H
|  | Flow | Speed | Head
|  | l/s | RPM | M
|  | 80 | 1440 | 30
Change in speed |  | 69 | 1242 | 22.3172
Note on G7: Corrected from 'x10' to 'x9.81': converts velocity head loss from metres of water to kPa (P = rho x g x h, with g = 9.81 m/s^2), consistent with the g-value already built into the G5 formula's 82711 constant. The previous x10 approximation understated the result by about 2%.

## data base (hidden)
description / item | consultant's | engineer's | pipe medium's | Pipe data
90 R Bend | Bassett's | C.Dearling | A.B.S (Thermoplastic - Class 4.5) |  | A.B.S (Thermoplastic - Class 4.5) |  |  |  | A.B.S (Thermoplastic - Class 6) |  |  |  | A.B.S (Thermoplastic - Class 9) |  |  |  | A.B.S (Thermoplastic - Class 10) |  |  |  | A.B.S (Thermoplastic - Class 12) |  |  |  | A.B.S (Thermoplastic - Class 15) |  |  |  | Coes-therm |  |  |  | Copper tube (Type A) |  |  |  | Copper tube (Type B)
Isolation Valve | Civil & Civic | C.Pinder | A.B.S (Thermoplastic - Class 6) | nominal | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass | inside | wall thk | Maximum | Mass
Tee - Line | EMF Griffith's | L.Ramah | A.B.S (Thermoplastic - Class 9) | dia | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m | dia | mm | Pressure kPa | kg/m
Tee - Branch | Lincolne Scott | M.Loveday | A.B.S (Thermoplastic - Class 10) | 15 | [20 empty] | 17.1 | 2.1 | 1500 | 0.14 |  |  |  |  | 12.7 | 1.02 | 6380 |  | 10.84
Reducer | Mienhardt | J.Smith | A.B.S (Thermoplastic - Class 12) | 20 | [20 empty] | 21.4 | 2.7 | 1500 | 0.22 |  |  |  |  | 19.05 | 1.42 | 5900
Non Return Valve | Q Build |  | A.B.S (Thermoplastic - Class 15) | 25 | [8 empty] | 29.4 | 2.1 | 900 | 0.23 | [8 empty] | 26.9 | 3.3 | 1500 | 0.35 |  |  |  |  | 25.4 | 1.63 | 5070
Chiller | WBM |  | Coes-therm | 32 | [8 empty] | 37 | 2.6 | 900 | 0.35 | [8 empty] | 34 | 4.1 | 1500 | 0.55 |  |  |  |  | 31.75 | 1.63 | 4010
Control Valve | N D Y |  | Copper tube (Type A) | 40 | [8 empty] | 42.3 | 3 | 900 | 0.45 | [8 empty] | 38.8 | 4.7 | 1500 | 0.7 |  |  |  |  | 38.1 | 1.63 | 3310
Cooling coil |  |  | Copper tube (Type B) | 50 | [8 empty] | 53 | 3.7 | 900 | 0.7 |  |  |  |  | 50.8 | 4.8 | 1200 | 0.9 | [8 empty] | 50.8 | 1.63 | 2460
Annubar |  |  | Galv Steel Pipe (Medium) | 65 | [20 empty] | 48.6 | 5.9 | 1500 | 1.1 |  |  |  |  | 63.5 | 1.63 | 1960
Griswald Valve |  |  | Heavy Steel Pipe | 80 |  |  |  |  | 81.5 | 3.7 | 600 | 1.1 | 78.1 | 5.4 | 900 | 1.6 |  |  |  |  | 74.9 | 7 | 1200 | 2 | 71.7 | 8.6 | 1500 | 2.4 |  |  |  |  | 76.2 | 2.03 | 2030
Straight pipe |  |  | Light Steel Pipe | 100 |  |  |  |  | 104.9 | 4.7 | 600 | 1.8 | 100.5 | 6.9 | 900 | 2.5 |  |  |  |  | 96.3 | 9 | 1200 | 3.3 | 92.3 | 11 | 1500 | 4 |  |  |  |  | 101.6 | 2.03 | 1520
Strainer |  |  | Medium Steel Pipe | 125 | [10 empty] | 900 | [17 empty] | 127 | 2.03 | 1210
Heat meter |  |  | P.V.C (Class 12) | 150 |  |  |  |  | 154.5 | 6.9 | 600 | 3.8 | 148.1 | 10.1 | 900 | 5.4 |  |  |  |  | 141.9 | 13.2 | 1200 | 7 | 135.9 | 16.2 | 1500 | 8.4 |  |  |  |  | 152.4 | 2.64 | 1310
|  |  | Stand WT Steel | 200 | 205.5 | 6.8 | 450 | 4.9 | 201.2 | 9 | 600 | 6.4 | 192.9 | 13.1 | 900 | 9.2 |  |  |  |  | 184.8 | 17.2 | 1200 | 11.8 | 177.1 | 21 | 1500 | 14.2 |  |  |  |  | 203.2 | 2.64 | 920
|  |  | Stainless Steel | 250 | 238 | 6 | 450 | 5 | 234 | 7.9 | 600 | 6.6 |  |  |  |  | 224 | 12.7 | 1000 | 10.3 | 220 | 15 | 1200 | 12.1 | 213 | 18.5 | 1500 | 14.6
|  |  |  | 300 | 300 | 7.5 | 450 | 7.8 | 295 | 9.8 | 600 | 10.2 |  |  |  |  | 283 | 16 | 1000 | 16.3 | 277 | 18.9 | 1200 | 19.1 | 268 | 23.3 | 1500 | 23.2
|  |  |  | 350 | 338 | 8.4 | 450 | 9.9 | 333 | 11.1 | 600 | 13 |  |  |  |  | 319 | 18 | 1000 | 20.6 | 312 | 21.3 | 1200 | 24.2 | 302 | 26.2 | 1500 | 29.4
|  |  |  | 400 | 381 | 9.4 | 450 | 12.6 | 375 | 12.4 | 600 | 16.4 |  |  |  |  | 360 | 20.2 | 1000 | 26.1 | 352 | 23.9 | 1200 | 30.7 | 341 | 29.5 | 1500 | 37.2
|  |  |  | 450 | 429 | 10.6 | 450 | 15.9 | 422 | 14 | 600 | 20.8 |  |  |  |  | 405 | 22.7 | 1000 | 33 | 396 | 27 | 1200 | 38.9 | 384 | 33.2 | 1500 | 47.1
|  |  |  | 500 | 476 | 11.8 | 450 | 19.6 | 469 | 15.5 | 600 | 25.5 |  |  |  |  | 450 | 25.2 | 1000 | 40.7
|  |  |  | 550 | 534 | 13.1 | 450 | 24.5 | 525 | 17.4 | 600 | 32.1
|  |  |  | 600 | 601 | 14.7 | 450 | 30.8 | 591 | 19.5 | 600 | 40.4
[5 empty] | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness |  |  |  | Absolute Roughness