## Chiller Efficiency Calc
HVAC - CHILLER EFFICIENCY CALCULATOR
kW/TR • COP • EER • Cooling Capacity (TR) — with formulas & industry reference ranges
HVAC Simplified™ ¦ hvacsimplified.in
1. EFFICIENCY FROM POWER INPUT & COOLING CAPACITY
Parameter | Value | Unit | Notes
Power Input (Electrical) | 200 | kW | Measured/rated compressor electrical input
Cooling Capacity | 284.3 | TR | 1 TR = 12,000 Btu/hr = 3.517 kW
kW/TR (Efficiency) | 0.70348 | kW/TR | Lower is more efficient
COP (Coefficient of Performance) | 4.9994 | — | COP = 3.517 / (kW/TR)
EER (Energy Efficiency Ratio) | 17.058 | Btu/W·hr | EER = 12 / (kW/TR)
2. COOLING CAPACITY (TR) FROM WATER FLOW — IP UNITS
Parameter | Value | Unit | Notes
Chilled Water Flow Rate | 680 | GPM | US Gallons per minute
Temperature Difference (ΔT) | 10 | °F | Return temp − Supply temp
Cooling Capacity (TR) | 283.3333 | TR | TR = GPM × ΔT(°F) × 500 / 12,000
3. COOLING CAPACITY (TR) FROM WATER FLOW — SI (METRIC) UNITS
Parameter | Value | Unit | Notes
Chilled Water Flow Rate | 43 | L/s | Litres per second
Temperature Difference (ΔT) | 5.5 | °C | Return temp − Supply temp
Cooling Load (Q) | 989.989 | kW | Q(kW) = Flow(L/s) × ΔT(°C) × 4.186
Cooling Capacity (TR) | 281.4868 | TR | 1 TR = 3.517 kW
4. TYPICAL CHILLER EFFICIENCY REFERENCE RANGES (AHRI 550/590 basis)
Chiller Type | Typical kW/TR | Typical COP | Notes
Air-Cooled Chiller (Scroll/Screw) | 1.05 – 1.20 | 2.9 – 3.3 | Standard efficiency, AHRI 550/590 rated
Air-Cooled Chiller (High Efficiency) | 0.85 – 1.00 | 3.5 – 4.1 | Premium efficiency / VFD-equipped
Water-Cooled Chiller (Screw) | 0.60 – 0.75 | 4.7 – 5.9 | Requires cooling tower loop
Water-Cooled Chiller (Centrifugal) | 0.50 – 0.65 | 5.4 – 7.0 | Large tonnage, high efficiency
Water-Cooled Chiller (Magnetic Bearing/VFD) | 0.35 – 0.50 | 7.0 – 10.0 | Best-in-class, part-load optimized
5. FORMULA REFERENCES
• AHRI Standard 550/590 (I-P) — Performance Rating of Water-Chilling and Heat Pump Water-Heating Packages Using the Vapor Compression Cycle
• ASHRAE Handbook — HVAC Systems and Equipment, Chapter 43 (Centrifugal & Rotary Screw Water Chillers)
• 1 Ton of Refrigeration (TR) = 12,000 Btu/hr = 3.517 kW (ASHRAE conversion constant)
• Sensible heat formula (IP): Q(Btu/hr) = GPM × ΔT(°F) × 500 → TR = Q / 12,000
• Sensible heat formula (SI): Q(kW) = Flow(L/s) × ΔT(°C) × 4.186 → TR = Q / 3.517
• COP = 3.517 / (kW/TR) ¦ EER (Btu/W·hr) = 12 / (kW/TR) — standard IP-to-SI efficiency conversions
Edit only the yellow input cells — all other cells recalculate automatically. Prepared by HVAC Simplified™.