## Plant Layout
CHILLER PLANT LAYOUT CALCULATOR
EFFICIENT • RELIABLE • EASY TO OPERATE & MAINTAIN
1. SYSTEM OVERVIEW
✓ The chiller plant produces chilled water that is circulated to AHUs / FCUs to remove heat from the building.
✓ Typical temperature set: Chilled Water Supply (CHWS) and Chilled Water Return (CHWR) are entered on the Input Parameters sheet; ΔT is calculated automatically.
✓ Primary equipment: Chiller(s), CHW Pumps, Cooling Tower, Condenser Water Pumps, Expansion Tank, BMS, Valves & Controls.
✓ All figures shown in the green boxes below are LIVE and pull from the Input Parameters / Design Calculations sheets — change your project data there and this summary updates automatically.
LIVE PROJECT SUMMARY (from Input Parameters)
Building Type | Total Cooling Load (TR) | No. of Chillers
Commercial Building | 1500 | 2
CHW ΔT (°C) | CHW Flow Rate (LPM) | CW Flow Rate (LPM)
5 | 15119.6561 | 18899.5701
2. FLOW DIAGRAM & 3. TYPICAL CHILLER PLANT LAYOUT (PLAN VIEW)
5. DESIGN NOTES
✓ Provide minimum 1000 mm clearance around equipment for operation & maintenance.
✓ Provide isolation valves at suction & discharge of all pumps.
✓ Provide strainers before chillers and pumps.
✓ Ensure vibration isolation for chillers and pumps.
✓ Provide proper drainage with slope; route floor drain away from equipment.
✓ Ensure adequate ventilation as per heat load (combustion/condenser air as applicable).
6. TYPICAL EQUIPMENT SEQUENCE
1. Cooling Tower rejects heat to atmosphere.
2. CWP (condenser water) pumps circulate condenser water to remove heat from the chiller.
3. Chiller removes heat from the building loop and produces chilled water.
4. CHW pumps distribute chilled water to AHUs / FCUs.
5. Chilled water returns to the plant through the return header.
6. Expansion tank maintains water pressure and absorbs thermal expansion.
7. BMS monitors and controls the entire system.
7. PIPING COLOR CODE
Service | Color
Chilled Water Supply (CHWS)
Chilled Water Return (CHWR)
Condenser Water Supply (CWS)
Condenser Water Return (CWR)
Drain / Overflow
Make-Up Water
Chemical Dosing Line
★ KEY TAKEAWAY: A well-designed chiller plant ensures energy efficiency, system reliability, easy maintenance and comfortable indoor environment. ¦ Good design today, better performance tomorrow.

## Input Parameters
INPUT PARAMETERS
Enter your project data in the YELLOW cells only. All other sheets calculate automatically from these values.
A. PROJECT / BUILDING DATA
Building Type | Commercial Building
Project Name | Enter project name
Total Cooling Load | 1500 | TR
No. of Chillers (duty) | 2 | no.
Standby Chillers | 0 | no.
Chiller Type | Water Cooled
B. CHILLED WATER (CHW) SIDE – PRIMARY LOOP
Chilled Water Supply Temp (CHWS) | 7 | °C
Chilled Water Return Temp (CHWR) | 12 | °C
Specific Heat of Water (Cp) | 4.187 | kJ/kg.°C
Water Density | 1000 | kg/m³
CHW Header Design Velocity | 2 | m/s
CHW Pump Total Head | 35 | m
CHW Pump Efficiency | 72% | -
C. CONDENSER WATER (CW) SIDE – SECONDARY LOOP
Condenser Water Supply Temp (CT → Chiller) | 30 | °C
Condenser Water Return Temp (Chiller → CT) | 35 | °C
Chiller Heat Rejection Factor | 1.25 | -
CW Header Design Velocity | 2.5 | m/s
CW Pump Total Head | 30 | m
CW Pump Efficiency | 72% | -
D. EXPANSION TANK SIZING INPUTS
Estimated System Water Volume | 15000 | L
Minimum System Temperature (fill) | 7 | °C
Maximum System Temp (static/idle) | 35 | °C
Expansion Tank Fill (Initial) Pressure | 1.5 | bar (g)
Max Allowable Pressure (relief set point) | 4 | bar (g)
E. DESIGN DATA REFERENCE (from original layout chart)
1 TR (Ton of Refrigeration) | 3.517 | kW (fixed constant, not editable)
Note on D10: Enter number of standby (N+1) chillers - not included in duty flow split.
Note on D16: Standard value for water ≈ 4.187 kJ/kg.°C. Adjust only if using glycol/brine (see note).
Note on D17: Approx. 1000 kg/m³ for chilled water 5-15°C.
Note on D18: Typical CHW main header velocity range: 1.5 - 2.5 m/s.
Note on D23: Cooler water leaving the cooling tower and entering the chiller condenser.
Note on D24: Warmer water leaving the chiller condenser (after absorbing heat) and returning to the cooling tower.
Note on D25: Condenser heat rejected ≈ Evaporator load × (1 + 1/COP). A factor of 1.20-1.30 is typical for water-cooled chillers (COP ≈ 4-5).
Note on D26: Typical CW main header velocity range: 2.0 - 3.0 m/s.
Note on D31: Sum of water volume in chiller(s), piping, coils and header. If unknown, a preliminary rule of thumb of 8-12 L per TR of installed capacity may be used.
Note on D33: Worst-case water temperature when system is static/idle (e.g. ambient before chiller start).

## Design Calculations
DESIGN CALCULATIONS
All cells below are formulas that recalculate automatically from the Input Parameters sheet. Do not overwrite green cells.
1. TOTAL COOLING LOAD
Total Cooling Load | 1500 | TR
Total Cooling Load (kW) | 5275.5 | kW (TR × 3.517)
Cooling Load per Chiller | 750 | TR / chiller
2. CHILLED WATER (CHW) SIDE
CHW ΔT (CHWR − CHWS) | 5 | °C
CHW Flow Rate | 15119.6561 | L/min (LPM)
CHW Flow Rate | 907.1794 | m³/hr
CHW Flow Rate | 3994.1898 | US gpm
CHW Flow Rate per Chiller | 7559.828 | L/min (LPM)
CHW Header Pipe — Recommended Internal Diameter | 400.5303 | mm (select nearest standard pipe size)
CHW Pump Power (per pump, hydraulic) | 60.0849 | kW
CHW Pump Power (per pump) | 80.5738 | HP
3. CONDENSER WATER (CW) SIDE
Condenser Heat Rejection | 6594.375 | kW (Evaporator load × Heat Rejection Factor)
CW ΔT (CW Return − CW Supply to chiller) | 5 | °C
CW Flow Rate | 18899.5701 | L/min (LPM)
CW Flow Rate | 1133.9742 | m³/hr
CW Flow Rate | 4992.7372 | US gpm
CW Header Pipe — Recommended Internal Diameter | 400.5303 | mm (select nearest standard pipe size)
CW Pump Power (per pump, hydraulic) | 64.3767 | kW
CW Pump Power (per pump) | 86.3291 | HP
Cooling Tower Duty (≈ Condenser Heat Rejection) | 1875 | TR (nominal CT selection duty)
Note on B12: Q(LPM) = (Load_kW × 60) / (Cp × ΔT) Derived from Q(kW) = mass flow(kg/s) × Cp(kJ/kg.°C) × ΔT(°C), with 1 L water ≈ 1 kg. NOTE ON ORIGINAL CHART: the source infographic showed 'Q = TR × 3.517 / ΔT' = 1,055 LPM for 1500 TR @ ΔT=5°C. That formula omits the water specific heat (4.187 kJ/kg.°C) and the sec-to-min conversion, understating flow by ~14x. The corrected result here (≈ 15,120 LPM) matches the standard HVAC rule of thumb of ~2.4 USgpm/ton at 10°F ΔT.

## Expansion Tank & Schedule
EXPANSION TANK SIZING & EQUIPMENT SCHEDULE
1. EXPANSION TANK SIZING (preliminary / diaphragm type)
Simplified ASHRAE-style method. Verify final selection against the manufacturer's sizing software using actual system water content and relief valve setting.
System Water Volume |  | 15000 | L
Volumetric Expansion Coefficient of Water (β, avg. over range) |  | 0.0003 | per °C (typical average, 5-50°C range)
System Temperature Rise (Max − Min) |  | 28 | °C
Expansion Volume |  | 126 | L
Acceptance Factor (based on fill / max pressure, atm = 1.013 bar) |  | 0.4987 | -
Required Expansion Tank Volume |  | 252.6552 | L → select next available standard tank size
2. EQUIPMENT SCHEDULE (fill in selected equipment against calculated duty)
Item | No. | Design Duty (calculated) | Selected Model / Capacity | Remarks
Chiller (Water Cooled) | 2 | 750 TR each
Chilled Water Pumps (Primary) | 2 | 7,560 LPM @ 35 m head
Condenser Water Pumps (Secondary) | 2 | 9,450 LPM @ 30 m head
Cooling Tower | 2 | 938 TR each (nominal)
Chilled Water Header | 1 | 401 mm dia. (recommended)
Expansion Tank | 1 | 253 L (min.)
BMS Panel | 1 | Monitors & controls entire plant
Yellow cells (Selected Model / Capacity, Remarks) are for the engineer to fill in once actual equipment is selected.
3. ASSUMPTIONS & REFERENCES
• 1 TR = 3.517 kW (fixed constant per ASHRAE).
• Water specific heat and density are editable on the Input Parameters sheet for glycol/brine mixes — replace with fluid supplier data if used.
• Pipe sizing uses continuity equation Q = A×V solved for internal diameter at the design velocity entered on the Input Parameters sheet; confirm against available standard pipe schedules (e.g. Sch 40 GI / carbon steel).
• Pump power is hydraulic (water) power only; add motor and drive losses per manufacturer curve for BHP/kW selection.
• Heat Rejection Factor approximates condenser duty from chiller COP; replace with manufacturer's rejection data at final selection stage.
• Expansion tank sizing is a simplified preliminary method — confirm with tank manufacturer's software using actual relief valve setting and static height.