## Cover
COMMERCIAL KITCHEN HOOD EXHAUST AIRFLOW CALCULATOR
NFPA 96 / IMC Section 507 / ASHRAE Kitchen Ventilation — Exhaust, Makeup Air & Duct Velocity Sizing Tool
Prepared for: Mr. Khan — HVAC / MEP Business Development & Technical Sales, Riyadh, Saudi Arabia
Published by HVAC Simplified
CONTENTS
1. Codes & Standards Referenced | Sheet: Codes & Standards
2. Appliance Duty Classification Reference | Sheet: Duty Classification
3. Type I Hood Exhaust Rate Table | Sheet: Type I Rates
4. Type II Hood Exhaust Rate Table | Sheet: Type II Rates
5. Exhaust Airflow Calculator (main tool) | Sheet: Calculator
6. Makeup Air & Grease Duct Velocity Check | Sheet: MUA & Duct Velocity
7. Overhang / Capture-Velocity Method (custom hoods) | Sheet: Capture Velocity Method
8. Notes, Assumptions & Disclaimer | Sheet: Notes & Disclaimer
⚠ Engineering reference tool. Always verify exhaust rates against the specific code edition and AHJ amendments adopted for the project jurisdiction — see the Notes & Disclaimer sheet.

## Codes & Standards
CODES & STANDARDS REFERENCED IN THIS WORKBOOK
Code / Standard | Full Title | What It Governs (used in this workbook) | Typical Edition Referenced
NFPA 96 | Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations | Primary source for hood type/duty exhaust rate tables, duct velocity, fire suppression triggers, clearances | 2021 Edition
IMC (International Mechanical Code) §507 | International Mechanical Code — Commercial Kitchen Hoods | Adopts/mirrors NFPA 96 exhaust rate tables (Table 507.2.1 / 507.2.2.1); Type I vs Type II hood requirements | 2021 Edition
ASHRAE Handbook — HVAC Applications, Ch. Kitchen Ventilation | ASHRAE Applications Handbook, Commercial Kitchen Ventilation chapter | Engineering basis for capture-velocity / overhang method, thermal plume behavior, makeup air design | Current Edition
UL 710 | Standard for Safety — Exhaust Hoods for Commercial Cooking Equipment | Listing/testing standard hoods must comply with; basis for reduced-flow proprietary hood ratings | Current Edition
UL 710B | Standard for Recirculating Systems | Referenced for grease-effluent test exception for certain electric appliances | Current Edition
UL 300 | Standard for Fire Testing of Fire Extinguishing Systems for Protection of Restaurant Cooking Areas | Wet chemical fire suppression system requirement triggered by Type I hood appliances | Current Edition
Local Fire/Energy Code Amendments (AHJ-specific) | e.g., Saudi Building Code (SBC), local Civil Defense fire code, Title 24 (CA), state mechanical codes | May adjust exhaust rate tables, DCKV requirements, or add local approval steps — always confirm with local AHJ | Per project

## Duty Classification
APPLIANCE DUTY CLASSIFICATION (per NFPA 96 / IMC Table 507.2.1)
Duty Classification | Typical Cooking Surface Temp. | Fuel/Effluent Basis | Representative Appliances
Light-Duty | < 450°F (232°C) | Low grease/smoke effluent | Ovens (convection, deck), steam kettles, steamers, pasta cookers, tilting skillets (light use)
Medium-Duty | 450°F – 600°F (232–316°C) | Moderate grease loading | Ranges (gas/electric), griddles, hot-top ranges, gas/electric conveyor pizza ovens, fryers
Heavy-Duty | 600°F – 700°F (316–371°C) | High grease loading | Charbroilers (gas/electric), woks, underfired broilers
Extra-Heavy-Duty | > 700°F (371°C) or solid fuel | Solid fuel / very high effluent | Solid-fuel broilers/ovens, wood or charcoal-fired equipment, solid-fuel pizza ovens
Rule: the hood is always sized to the HEAVIEST-duty appliance installed beneath it, not an average.

## Type I Rates
TYPE I HOOD — MINIMUM EXHAUST FLOW RATE (CFM per Linear Foot of Hood Length)
Source: IMC Table 507.2.1 basis / NFPA 96 — figures shown are representative; confirm exact edition adopted by local AHJ
Hood Type | Light-Duty | Medium-Duty | Heavy-Duty | Extra-Heavy-Duty | Notes
Wall-mounted canopy | 150 | 200 | 300 | 400 | Open on 3 sides (back against wall)
Single island canopy | 280 | 350 | 420 | 490 | Open on all 4 sides — higher rate due to no wall to block spillage
Double island canopy (per side) | 175 | 210 | 280 | 385 | Back-to-back over two cooking lines; rate applies per side
Eyebrow hood | 175 | 175 | NA | NA | Mounted directly on equipment; NOT permitted for heavy/extra-heavy duty
Backshelf / pass-over hood | 200 | 210 | 300 | NA | No overhang; NOT permitted for extra-heavy duty
Proximity / low-profile hood | Per mfr. UL 710 listing | Per mfr. UL 710 listing | Per mfr. UL 710 listing | Per mfr. UL 710 listing | Proprietary engineered design — uses tested rate, not table rate

## Type II Rates
TYPE II HOOD — MINIMUM EXHAUST FLOW RATE (CFM per Linear Foot of Hood Length)
Source: IMC / NFPA 96 Type II hood table — for heat/steam/moisture-only appliances (no grease). Light & Medium duty equipment only.
Hood Type | Light-Duty | Medium-Duty | Notes
Wall-mounted canopy | 200 | 300 | Dishwashers, steamers, ovens (non-grease)
Single island canopy | 400 | 500 | Open on all 4 sides
Double island canopy (per side) | 250 | 300 | Rate applies per side
Eyebrow hood | 250 | 250 | Mounted directly on equipment
Backshelf / pass-over hood | 200 | 300

## Calculator
lists (do not delete)
KITCHEN HOOD EXHAUST AIRFLOW CALCULATOR — TYPE I / TYPE II |  | Type I | Wall-mounted canopy | Light-Duty
Yellow cells = your inputs. All other cells calculate automatically from the code tables on the 'Type I Rates' / 'Type II Rates' sheets. |  | Type II | Single island canopy | Medium-Duty
|  |  | Double island canopy (per side) | Heavy-Duty
INPUTS |  |  | Eyebrow hood | Extra-Heavy-Duty
1. Hood Category | Type I |  | Backshelf / pass-over hood
2. Hood Type | Wall-mounted canopy
3. Appliance Duty Classification (heaviest appliance under hood) | Medium-Duty
4. Hood Length (linear feet) | 12
RESULTS
Exhaust rate per linear foot (cfm/ft) | 200
Required Exhaust Airflow (CFM) | 2400
Required Exhaust Airflow (L/s) [1 cfm = 0.4719 L/s] | 1132.56
Note on C8: Use the HEAVIEST duty appliance located under this hood section, per NFPA 96 rule. See 'Duty Classification' sheet.
Note on C9: Enter the actual hood length in feet, measured along the front of the hood.

## MUA & Duct Velocity
MAKEUP AIR & GREASE DUCT VELOCITY CHECK
A. MAKEUP AIR (MUA)
Required Exhaust Airflow (from Calculator sheet, cfm) | 2400
Makeup Air Replacement (% of exhaust) — typical 80-100% | 90%
Required Makeup Air (CFM) | 2160
Max direct hood-cavity replacement air (NFPA 96 cap = 10% of hood exhaust) | 240
B. GREASE DUCT VELOCITY CHECK
Exhaust Airflow (cfm) — from above | 2400
Proposed Duct Width (inches) | 16
Proposed Duct Height (inches) | 12
Duct Cross-Section Area (sq ft) | 1.3333
Resulting Duct Velocity (fpm) | 1800
NFPA 96 Minimum Required Velocity (fpm) | 1500
Velocity Check | OK — meets minimum velocity
Note on C16: NFPA 96 typically requires 1500 fpm minimum in grease duct (some jurisdictions/duct types allow 500 fpm for listed grease duct systems). Confirm with the adopted code edition.

## Capture Velocity Method
OVERHANG / CAPTURE-VELOCITY METHOD (Custom & Non-Standard Hoods)
ASHRAE engineering method: Q = V x A. Used where hood geometry falls outside the standard code tables (custom canopy, unusual overhang, engineered low-cfm hood).
Target Capture Velocity, V (fpm) — typical 100-150 fpm at hood face/perimeter | 125
Hood Open Perimeter Length, P (ft) — sum of all open (non-wall) sides | 20
Hood Height Above Cooking Surface, H (ft) | 4
Free (capture) Area, A = P x H (sq ft) | 80
Required Exhaust Airflow, Q = V x A (CFM) | 10000
Note: overhang beyond the appliance footprint (typically 6"-24" front/side/back depending on hood type per NFPA 96) reduces required cfm by improving plume capture before spillage. This method requires engineering judgment and is normally used to justify a reduced flow vs. the prescriptive table, subject to AHJ / hood manufacturer UL 710 listing approval.

## Notes & Disclaimer
NOTES, ASSUMPTIONS & DISCLAIMER
1. Exhaust rate figures on the 'Type I Rates' and 'Type II Rates' sheets are representative values drawn from the IMC Table 507.2.1 / NFPA 96 framework. Published cfm/linear-ft figures vary between code editions and local amendments (values as low as 140 cfm/ft and as high as 200+ cfm/ft for wall-mounted canopy, light duty, have been observed across different adopted editions) — always confirm the exact table in force for the project's jurisdiction (in KSA: local Civil Defense / Saudi Building Code adoption of NFPA 96) before issuing for design or submittal.
2. The hood is always sized to the heaviest-duty appliance located beneath it, not an average or a per-appliance sum.
3. Proximity, low-profile, and other proprietary engineered hoods are typically UL 710 tested and listed at a manufacturer-specific reduced flow rate — use the manufacturer's certified data sheet instead of the generic table rate for these products.
4. Makeup air (MUA) percentage (80-100% of exhaust) is a common design assumption, not a fixed code minimum — confirm against project-specific pressure balance and code requirements.
5. NFPA 96 duct velocity requirements vary by duct construction/listing; 1500 fpm minimum is the commonly cited conventional grease-duct minimum, but some listed/engineered systems permit lower velocities — verify against the adopted code edition.
6. This workbook is a preliminary engineering reference/screening tool. It does not replace a stamped mechanical engineering calculation, manufacturer hood certification (UL 710), or AHJ plan review and approval.
7. All formulas in the 'Calculator', 'MUA & Duct Velocity', and 'Capture Velocity Method' sheets recalculate automatically — only edit the yellow input cells.