## Design Calculations
WATER SUPPLY SYSTEM DESIGN CALCULATOR — HIGH-RISE BUILDING
Reliable Supply • Adequate Pressure • Efficient Design • Water Conservation (per CPHEEO Manual / NBC 2016 / IS 1172)
PROJECT INFORMATION
Project Name | Enter project name
Location | Riyadh, Saudi Arabia
Prepared By | Enter name
Date | Enter date
1. DESIGN BASIS
Building Type | Residential |  | Select from dropdown
No. of Floors (as described) | G+20 |  | Descriptive label only (e.g. G+20)
No. of Floors used in Calculation | 20 | floors | Habitable floors used for height & population below
Floor-to-Floor Height | 3.2 | m
Total Building Height | 64 | m | Formula: No. of floors x floor height
No. of Units per Floor | 4 | nos.
Unit Type | 4BHK
Persons per Unit | 5 | persons
Total Population Served | 400 | persons | Formula: floors x units/floor x persons/unit
Water Supply Source | Municipal + Underground Sump (UG Sump)
System Type | Overhead Tank with Booster Pump System
Design Standards Reference | CPHEEO Manual + NBC 2016 + IS 1172
2. WATER DEMAND CALCULATION
Per Capita Water Demand | 135 | lpcd | Typical range for Residential: see Reference sheet
Total Average Daily Demand | 54000 | L/day | Formula: population x per-capita demand
Total Average Daily Demand | 54 | m3/day
Peak Day Factor | 1.8 | - | CPHEEO recommended = 1.8
Maximum Day Demand | 97.2 | m3/day | Formula: avg daily demand x peak day factor
Peak Hour Factor | 2.7 | - | CPHEEO: ~2.7 for population < 50,000
DESIGN FLOW (Max Hour Demand) | 10.935 | m3/hr | Formula: (max day demand / 24) x peak hour factor — used throughout
3. OVERHEAD TANK (OHT) SIZING
Storage Capacity Fraction of Daily Demand | 0.3333 | - | Typically 1/3 to 1/2 of daily demand (NBC)
Required OHT Capacity | 17.9982 | m3 | Formula: avg daily demand x storage fraction
Adopted OHT Capacity | 20 | m3 | Auto-rounded up to next 5 m3; verify vs. market-available tank size
Tank Internal Length | 4.5 | m
Tank Internal Width | 2.5 | m
Tank Water Depth | 1.8 | m
Provided Tank Volume | 20.25 | m3 | Formula: L x W x Depth
Tank Capacity Check | OK - Adequate
4. BOOSTER PUMP SELECTION
Design Flow, Q | 10.935 | m3/hr | linked from Section 2
Design Flow, Q | 0.0030375 | m3/s | Formula: Q(m3/hr) / 3600
Static Head (Building Height) | 64 | m | linked from Section 1
Friction Head Allowance | 12 | m | Assume, or calculate via Hazen-Williams for actual pipe run
Residual Head Required at Top Floor | 10 | m | Min. 7-10 m typical (verify with local code)
Total Dynamic Head (TDH) | 86 | m | Formula: static head + friction head + residual head
Water Density | 1000 | kg/m3
Pump Efficiency | 65% | - | Enter as fraction (0.65 = 65%)
Hydraulic Power Required | 3.9425 | kW | P = rho x g x Q(m3/s) x TDH / (eff x 1000)
Power Required | 5.287 | HP | Formula: kW / 0.7457
No. of Duty (Working) Pumps | 1 | nos.
No. of Standby Pumps | 1 | nos.
Pump Configuration | 1W + 1S
Selected Standard Motor Rating (each pump) | 5.5 | HP | Next available standard rating >= power required
Selected Standard Motor Rating (each pump) | 4.1014 | kW
5. RISER (RISING MAIN) DESIGN
Design Flow, Q | 10.935 | m3/hr | linked from Section 2
Design Flow, Q | 0.0030375 | m3/s
Adopted Flow Velocity | 1.5 | m/s | Recommended range: 1.0 - 2.0 m/s
Calculated Riser Diameter | 0.050777 | m | D = SQRT(4Q / (pi x V))
Calculated Riser Diameter | 50.7771 | mm
Adopted Riser Size (NB) | 65 | mm | Next standard pipe size >= calculated diameter
6. PRESSURE CHECK AT TOP FLOOR
Static Pressure at Top Floor | 6.2784 | bar | P = rho x g x H / 100,000
Friction Loss in Riser | 1.1772 | bar | Derived from Friction Head (Sec. 4) for consistency
Available Pressure at Top Floor | 5.1012 | bar | Formula: static pressure - friction loss
Required Residual Pressure at Top Floor | 0.981 | bar | Derived from Residual Head (Sec. 4) for consistency
Pressure Adequacy Check | OK - Adequate
Note | Pressure at lower floors will be higher than top floor. Provide a Pressure Reducing Valve (PRV) if required to limit excess pressure at lower floors (typically < 3.5-4 bar at fixtures).
7. PIPE SIZE SUMMARY
Section | Flow Low (m3/hr) | Flow High (m3/hr) | Velocity Low (m/s) | Velocity High (m/s) | Calculated Dia (mm) | Adopted Size (mm NB)
Rising Main (Riser) | 10.935 | 10.935 | 1 | 2 | 50.7771 | 65
Floor Distribution Main | 1.5 | 2 | 0.6 | 1.5 | 34.3355 | 40
Branch to Kitchen Sink | 0.25 | 0.5 | 0.6 | 1.5 | 17.1677 | 20
Branch to Wash Basin | 0.1 | 0.25 | 0.6 | 1.5 | 12.1394 | 15
Branch to Shower | 0.1 | 0.25 | 0.6 | 1.5 | 12.1394 | 15
Branch to W.C. | 0.1 | 0.25 | 0.6 | 1.5 | 12.1394 | 15
Notes
8. DESIGN CHECKLIST
Water demand calculated | [DONE]
Overhead tank sized | [DONE]
Tank capacity adequate | [OK]
Booster pump selected | [DONE]
Riser size calculated | [DONE]
Pressure at top floor checked | [OK]
Floor distribution pipe sizes set | [DONE]
Valves, air release & drain points provided | Verify on drawings
9. KEY DESIGN NOTES
• Ensure minimum 1.0 bar pressure is available at the top floor fixtures.
• Maintain flow velocity within the recommended range (1.0-2.0 m/s in risers, 0.6-1.5 m/s in branches).
• Provide a standby pump for uninterrupted supply (typical duty: 1 Working + 1 Standby).
• Follow CPHEEO Manual / NBC 2016 / IS 1172 guidelines and local municipal code for final design.
• System components: UG Sump, Booster Pump Set, NRV/Gate Valves/Pressure Gauge, Rising Main (Riser), Overhead Tank with Float Valve, Distribution Piping, Air Release Valve, Drain Valve, PRV (if required), Water Meter (if by-law requires).
GOOD DESIGN DELIVERS WATER WHERE IT IS NEEDED, WHEN IT IS NEEDED, AT THE RIGHT PRESSURE.
Note on C52: CORRECTION: The original hand-drawn reference chart this sheet is based on stated 4.07 kW here, but recalculating its own formula (P = rho x g x Q x H / eta, with Q converted to m3/s) gives 3.94 kW. This cell uses the corrected formula. The final selected standard motor rating (5.5 HP) is unaffected either way.

## Std Sizes & Reference
REFERENCE TABLES & STANDARD SIZES
Standard Pipe Sizes (NB, mm) | Standard Pump Motor Ratings (HP) |  | Typical Water Demand (CPHEEO / NBC 2016)
15 | 0.5 |  | Residential (with sewerage) | 135 | lpcd
20 | 1 |  | Residential (higher income) | 150-200 | lpcd
25 | 1.5 |  | Hotel (per bed) | 180 | lpd/bed
32 | 2 |  | Hospital >100 beds (per bed) | 450 | lpd/bed
40 | 3 |  | Office / Commercial (per person) | 45 | lpcd
50 | 5 |  | School (per student, day) | 45 | lpcd
65 | 5.5 |  | Restaurant (per seat) | 70 | lpd/seat
80 | 7.5
100 | 10 |  | Source: CPHEEO Manual on Water Supply & Treatment; NBC 2016 Part 9
125 | 12.5
150 | 15
200 | 20
250 | 25
300 | 30
40
(CPVC/UPVC/PP-R/GI standard nominal bore sizes) | 50
60
75
100
(Typical commercially available motor/pump ratings)
Peak Factors (CPHEEO Manual)
| Max Daily Demand Factor | 1.8 (x avg daily demand)
| Max Hourly Demand Factor | 2.7 (population < 50,000)
| Max Hourly Demand Factor | 1.5 - 2.0 (population > 1,000,000)
Building Type List (dropdown source)
Residential
Residential (Luxury)
Hotel
Hospital
Office/Commercial
School
Mixed Use

## Legend & Assumptions
LEGEND, ASSUMPTIONS & CORRECTIONS
COLOR LEGEND
Blue text, yellow fill — Engineer input — edit these cells for your project.
Black text, white fill — Calculated automatically — do not overwrite.
Green text — Linked from another section/sheet — do not overwrite.
Bold value in pale blue fill — Key result cell (design flow, power, adopted sizes, checks).
HOW TO USE THIS WORKBOOK
1. Go to the 'Design Calculations' sheet and fill in every yellow-highlighted (blue text) input cell with your project's actual data.
2. All formula cells recalculate automatically as you change inputs — no manual re-entry needed.
3. Adopted pipe sizes and pump motor ratings auto-select the next available standard size from the 'Std Sizes & Reference' sheet; add/edit that list if your supplier's range differs.
4. Check Section 3 (Tank Capacity Check), Section 6 (Pressure Adequacy Check), and Section 8 (Design Checklist) for pass/fail results before finalizing.
5. Values in green are linked from earlier sections — change the source cell, not the linked cell.
CORRECTIONS MADE vs. THE ORIGINAL REFERENCE CHART
1. Booster pump power: the original chart's own formula (P = rho x g x Q x H / eta) works out to 3.94 kW, not the 4.07 kW shown. This has been corrected here — it does not change the final pump selection, which still rounds up to a standard 5.5 HP motor either way.
2. Friction loss (bar) and required residual pressure (bar) in the pressure check are now derived directly from the Friction Head (m) and Residual Head (m) inputs used for the pump TDH calculation (p = rho x g x h / 100,000), instead of being separate, disconnected assumptions — so both sections stay consistent automatically if you change either value.
3. All pipe sizes (riser and branches) now auto-select the nearest standard NB size >= the calculated diameter from a standard sizes table, instead of being fixed numbers.
4. The pump motor rating auto-selects the nearest standard HP rating >= the calculated power requirement.
5. Overhead tank capacity auto-rounds the calculated requirement up to the next 5 m3 increment; confirm the final figure against tanks actually available from your supplier.
6. 'No. of Floors (G+20)' is kept as a descriptive label only; a separate numeric 'No. of Floors used in Calculation' input drives the height and population formulas, since the original chart's population and height figures were both based on 20 floors rather than 21 (G + 20).
KEY ASSUMPTIONS & STANDARDS REFERENCED
• Per capita water demand, peak day/hour factors: CPHEEO Manual on Water Supply and Treatment.
• Overhead tank capacity: 1/3 to 1/2 of average daily demand, per NBC 2016 Part 9.
• Pipe velocity ranges: 1.0-2.0 m/s in risers/rising mains, 0.6-1.5 m/s in branch/distribution piping — typical plumbing design practice.
• Minimum residual pressure at the topmost fixture: commonly 1.0 bar (~10 m head); confirm against local plumbing code.
• Friction head/loss is an assumed allowance in this template; for detailed design, calculate actual friction loss using the Hazen-Williams or Darcy-Weisbach equation based on actual pipe lengths, fittings, and material roughness.
• Standard pipe and pump sizes listed are typical commercially available ranges — verify against your specific supplier/manufacturer catalogue.